## System Profile Inputs
System Profile Inputs |  |  |  |  | System Design Output (Optimization) | Tower Load (Kw) | PV Size (kWp) | Battery Ah | DG (kva) | Modules | Array | DOD | PV Design Factor | DG Contribution | PV Losses | Inv. Efficiency | DG Design Factor | PF | PV Contribution Direct | Specific Yield (kwh/kWp/day)
|  | PV Syst Profile |  |  |  | 1 | 7.0651 | 854.1124 | 13.8235 | 325Wp | 2.60kWp | 50% | 0% | 0% | 9% | 92% | 0% | 1 | 35% | 4.9064
Tower Profile |  | Specific Production (kwh/kWp/Yr) - PV Syst | 1551.0839
|  | Specific Yield (kwh/kWp/day) - PV Syst | 4.2495
Tower Load Servicing (in Hrs) | 24 | Specific Production (kwh/kWp/Yr) Actual best 8 months | 1192.2491 |  | Batch1 (57 sites)
Rectifier Charging Efficiency | 94% | Specific Yield (kwh/kWp/day) Actual best 8 months | 4.9064 |  | System Configuration | 1.008 | 10.88 | 600 | 20 | 340Wp | 2.72kWp | 70% | 15% | 30% | 15% | 92% | 0% | 0.9 | 0% | 4.5
[5 empty] | Design Calculation | 1.01 | 8.1213 | 1327.1592 | 21.674
Battery Profile |  | PV Profile |  |  | Batch2 (50 Sites)
Battery Contribution to service tower load as per the PV syst (Avg.) (in %) | 65% | PV Contribution to service tower load as per the PV syst (Avg.) (in %) (DIRECT) (Rest of the total will be through Battery) | 35% |  | System Configuration | 1 | 7.92 | 600 | 20 | 330Wp | 2.64kWp | 70% | 15% | 30% | 15% | 92% | 0% | 1 | 0% | 4.5
Battery DOD (in %) | 50% | PV Loss due to temperature as per the PV Syst (in%) | 6% |  | Design Calculation | 1 | 8.0409 | 1314.019 | 21.4594
Battery WH Efficiency (in %) | 88% | Mismatch/ Ohmic /Degradation Loss (in %) | 3%
Battery AH Efficiency (in %) | >95% | MPPT Charging Efficiency | 95%
Battery Bank Voltage (in Volts) | 48 | Inverter Efficiency | 92%
Battery Bank Charging Voltage (in Volts) | 55 | PV Design Factor | 0%
Battery Bank charging Current (in %) | 20% | PV table of 330Wp*8 (in kWp) | 2.64 | Batch2
|  | PV table of 325Wp*8 (in kWp) | 2.6
DG Profile |  | PV table of 340Wp*8 (in kWp) | 2.72 | Batch1
DG Contribution to service tower load as per the PV syst (Avg.) (in %) | 0% | Inverter Design Factor | 1.2
Rectifier Charging Efficiency | 94% | Rectifier Design Factor | 1.2 |  | Indicators:-
Battery Bank Charging Voltage (in Volts) | 55 | STC Irradiance (W/sqmtrs) | 1000 |  |  | System Profile Inputs through Drop-Downs
Battery Bank charging Current (in %) | 20% | STC Cell Temp (Deg C) | 25 |  |  | System Design Results
DG Design Factor (in%) | 0% | NOCT at 800w/sqm, Amb Temp 20degC, wind 1m/s (degC) | 44 |  | Rest of the data | Hard Coded
|  | LID (Light Induced Degradation) | 2%
|  | Annual Degradation (Linear) | 0.7%
|  | IAM (Incedent Angle Modifier) Loss | 2%

## System Design Results
Site Specifications - As Built
| Sno. | Tower Load (Kw) | PV (kWp) | Battery Bank 48V (Ah) | Genset (kVA) | Genset Type | List for Drop Down | Total Energy Demand of site in KWH (O/P of Inverter -AC) | Battery Sizing (in kwh) @ |  |  | Battery AH | PV Sizing for DIRECT contribution of KWH @ (65% will be through Battey) | PV (kWp) | DG Sizing in KVA with contribution of kwh | PV to MPPT O/p (kwh) | MPPT to Load (kwh) | MPPT to Battery (Rate of Charging) (kwh/Hr) | MPPT to Battery (kwh) | Battery to Load (kwh) | DG to Load (kwh) | DG to Battery (kwh) | Validation
[8 empty] | Load Hrs | Contribution | Efficiency | DOD | Volts | Contribution | Contribution | Contribution |  | Contribution | 55 |  |  | Contribution | Contribution | Energy available at (MPPT+DG) O/p > Load requirement | (4.5*Rate of charge of battery from (MPPT+DG) - Energy supplied by Battery per day) > 0 | UnUsed Energy (4.5*Rate of Charge-MPPT to Battery) > 0 | (MPPT to Battery*Battery Eff.+DG to Battery*Battery Eff. - Battery to Load) > 0
[8 empty] | 24 | 65% | 88% | 50% | 48 | 35% | 35% | 0% |  | 35% | 20% |  |  | 0% | 0%
Batch2 | 1 | 0.8 | 5.28 | 600 | 20 | 3 Ph | 0.8_DC | 19.2 | 28.3636 |  |  | 590.9091 | 23.9821 | 4.8879 | 9.7074 | 20.7325 | 6.72 | 6.5 | 14.0125 | 12.48 | 0 | 0 | 1.5325 | 19.4114 | 17.8789 | -0.14899
Batch1 | 2 | 0.846 | 8.16 | 600 | 20 | 3 Ph | 0.846 | 21.6 | 34.6838 |  |  | 722.5791 | 29.3259 | 5.9771 | 11.6946 | 25.3523 | 8.2174 | 7.9484 | 17.1349 | 13.3826 | 0 | 0 | 3.7523 | 25.6151 | 21.8628 | 1.6961
Batch1 | 3 | 0.864 | 8.16 | 600 | 20 | 1 Ph | 0.864 | 22.0596 | 35.4217 |  |  | 737.9531 | 29.9499 | 6.1043 | 11.9435 | 25.8917 | 8.3922 | 8.1175 | 17.4994 | 13.6673 | 0 | 0 | 3.8321 | 26.1601 | 22.328 | 1.7322
| 4 | 0.909 | 8.16 | 600 | 20 | 3 Ph | 0.909 | 23.2085 | 37.2666 |  |  | 776.3881 | 31.5098 | 6.4222 | 12.5655 | 27.2402 | 8.8293 | 8.5403 | 18.4109 | 14.3792 | 0 | 0 | 4.0317 | 27.5226 | 23.4909 | 1.8224
Batch1 | 5 | 0.927 | 8.16 | 600 | 20 | 3 Ph | 0.927 | 23.6681 | 38.0046 |  |  | 791.7622 | 32.1337 | 6.5494 | 12.8143 | 27.7796 | 9.0042 | 8.7094 | 18.7754 | 14.6639 | 0 | 0 | 4.1115 | 28.0676 | 23.9561 | 1.8585
| 6 | 0.972 | 8.16 | 600 | 20 | 3 Ph | 0.972 | 24.817 | 39.8495 |  |  | 830.1972 | 33.6936 | 6.8673 | 13.4364 | 29.1281 | 9.4413 | 9.1322 | 19.6869 | 15.3758 | 0 | 0 | 4.3111 | 29.4301 | 25.119 | 1.9487
Batch2 | 7 | 1 | 7.92 | 600 | 20 | 3 Ph | 1 | 25.5319 | 40.9974 |  |  | 854.1124 | 34.6642 | 7.0651 | 13.8235 | 29.9672 | 9.7132 | 9.3952 | 20.254 | 15.8187 | 0 | 0 | 4.4353 | 30.2779 | 25.8426 | 2.0048
| 8 | 1.008 | 10.88 | 600 | 20 | 3 Ph | 1.008 | 25.7362 | 41.3254 |  |  | 860.9453 | 34.9415 | 7.1217 | 13.934 | 30.2069 | 9.7909 | 9.4704 | 20.416 | 15.9452 | 0 | 0 | 4.4708 | 30.5201 | 26.0493 | 2.0209
| 9 | 1.017 | 10.88 | 600 | 20 | 3 Ph | 1.017 | 25.966 | 41.6943 |  |  | 868.6323 | 35.2535 | 7.1852 | 14.0585 | 30.4767 | 9.8784 | 9.555 | 20.5983 | 16.0876 | 0 | 0 | 4.5107 | 30.7926 | 26.2819 | 2.0389
Batch2 | 10 | 1.021 | 10.56 | 600 | 20 | 3 Ph | 1.021 | 26.0681 | 41.8583 |  |  | 872.0487 | 35.3922 | 7.2135 | 14.1137 | 30.5965 | 9.9172 | 9.5925 | 20.6793 | 16.1509 | 0 | 0 | 4.5284 | 30.9137 | 26.3853 | 2.0469
| 11 | 1.026 | 10.88 | 600 | 20 | 3 Ph | 1.026 | 26.1957 | 42.0633 |  |  | 876.3193 | 35.5655 | 7.2488 | 14.1829 | 30.7464 | 9.9658 | 9.6395 | 20.7806 | 16.23 | 0 | 0 | 4.5506 | 31.0651 | 26.5145 | 2.0569
| 12 | 1.035 | 10.88 | 600 | 20 | 3 Ph | 1.035_DC | 24.84 | 36.6955 |  |  | 764.4886 | 31.0268 | 6.3238 | 12.559 | 26.8227 | 8.694 | 8.4094 | 18.1287 | 16.146 | 0 | 0 | 1.9827 | 25.1135 | 23.1309 | -0.19275
| 13 | 1.044 | 10.88 | 600 | 20 | 3 Ph | 1.044 | 26.6553 | 42.8013 |  |  | 891.6933 | 36.1894 | 7.376 | 14.4317 | 31.2858 | 10.1406 | 9.8086 | 21.1452 | 16.5147 | 0 | 0 | 4.6304 | 31.6101 | 26.9796 | 2.093
| 14 | 1.1 | 7.92 | 600 | 20 | 3 Ph | 1.1_DC | 26.4 | 39 |  |  | 812.5 | 32.9754 | 6.7209 | 13.3477 | 28.5072 | 9.24 | 8.9375 | 19.2672 | 17.16 | 0 | 0 | 2.1072 | 26.6907 | 24.5835 | -0.20486
| 15 | 1.1 | 7.92 | 600 | 20 | 3 Ph | 1.1_DC | 26.4 | 39 |  |  | 812.5 | 32.9754 | 6.7209 | 13.3477 | 28.5072 | 9.24 | 8.9375 | 19.2672 | 17.16 | 0 | 0 | 2.1072 | 26.6907 | 24.5835 | -0.20486
| 16 | 1.1 | 7.92 | 600 | 20 | 1 Ph | 1.1 | 28.0851 | 45.0971 |  |  | 939.5236 | 38.1306 | 7.7717 | 15.2058 | 32.9639 | 10.6846 | 10.3348 | 22.2794 | 17.4006 | 0 | 0 | 4.8788 | 33.3056 | 28.4268 | 2.2053
| 17 | 1.107 | 10.88 | 600 | 20 | 3 Ph | 1.107 | 28.2638 | 45.3841 |  |  | 945.5024 | 38.3733 | 7.8211 | 15.3026 | 33.1737 | 10.7525 | 10.4005 | 22.4212 | 17.5113 | 0 | 0 | 4.9099 | 33.5176 | 28.6077 | 2.2193
Batch2 | 18 | 1.11 | 7.92 | 600 | 20 | 3 Ph | 1.11_DC | 26.64 | 39.3545 |  |  | 819.8864 | 33.2751 | 6.782 | 13.4691 | 28.7664 | 9.324 | 9.0188 | 19.4424 | 17.316 | 0 | 0 | 2.1264 | 26.9334 | 24.807 | -0.20672
| 19 | 1.125 | 10.88 | 600 | 20 | 3 Ph | 1.125 | 28.7234 | 46.1221 |  |  | 960.8764 | 38.9972 | 7.9483 | 15.5514 | 33.7131 | 10.9274 | 10.5696 | 22.7857 | 17.796 | 0 | 0 | 4.9897 | 34.0626 | 29.0729 | 2.2554
| 20 | 1.152 | 10.88 | 600 | 20 | 3 Ph | 1.152_DC | 27.648 | 40.8436 |  |  | 850.9091 | 34.5342 | 7.0386 | 13.9787 | 29.8548 | 9.6768 | 9.36 | 20.178 | 17.9712 | 0 | 0 | 2.2068 | 27.9525 | 25.7457 | -0.21454
| 21 | 1.161 | 10.88 | 600 | 20 | 3 Ph | 1.161 | 29.6426 | 47.598 |  |  | 991.6244 | 40.2451 | 8.2026 | 16.049 | 34.7919 | 11.2771 | 10.9079 | 23.5149 | 18.3655 | 0 | 0 | 5.1494 | 35.1526 | 30.0032 | 2.3276
| 22 | 1.188 | 10.88 | 600 | 20 | 3 Ph | 1.188_DC | 28.512 | 42.12 |  |  | 877.5 | 35.6134 | 7.2586 | 14.4156 | 30.7878 | 9.9792 | 9.6525 | 20.8086 | 18.5328 | 0 | 0 | 2.2758 | 28.826 | 26.5502 | -0.22125
| 23 | 1.188 | 10.88 | 600 | 20 | 3 Ph | 1.188_DC | 28.512 | 42.12 |  |  | 877.5 | 35.6134 | 7.2586 | 14.4156 | 30.7878 | 9.9792 | 9.6525 | 20.8086 | 18.5328 | 0 | 0 | 2.2758 | 28.826 | 26.5502 | -0.22125
| 24 | 1.197 | 10.88 | 600 | 20 | 3 Ph | 1.197 | 30.5617 | 49.0739 |  |  | 1022.3725 | 41.4931 | 8.457 | 16.5467 | 35.8707 | 11.6267 | 11.2461 | 24.244 | 18.935 | 0 | 0 | 5.309 | 36.2426 | 30.9336 | 2.3998
| 25 | 1.2 | 7.92 | 600 | 20 | 3 Ph | 1.2_DC | 28.8 | 42.5455 |  |  | 886.3636 | 35.9731 | 7.3319 | 14.5612 | 31.0988 | 10.08 | 9.75 | 21.0188 | 18.72 | 0 | 0 | 2.2988 | 29.1172 | 26.8184 | -0.22348
| 26 | 1.2 | 7.92 | 600 | 20 | 3 Ph | 1.2 | 30.6383 | 49.1969 |  |  | 1024.9348 | 41.5971 | 8.4782 | 16.5881 | 35.9607 | 11.6559 | 11.2743 | 24.3048 | 18.9824 | 0 | 0 | 5.3224 | 36.3334 | 31.0111 | 2.4058
Batch1 | 27 | 1.215 | 10.88 | 1000 | 20 | 3 Ph | 1.215_DC | 29.16 | 43.0773 |  |  | 897.4432 | 36.4228 | 7.4236 | 14.7432 | 31.4875 | 10.206 | 9.8719 | 21.2815 | 18.954 | 0 | 0 | 2.3275 | 29.4811 | 27.1536 | -0.22628
| 28 | 1.224 | 10.88 | 1000 | 20 | 3 Ph | 1.224 | 31.2511 | 50.1808 |  |  | 1045.4335 | 42.429 | 8.6477 | 16.9199 | 36.6799 | 11.889 | 11.4998 | 24.7909 | 19.3621 | 0 | 0 | 5.4288 | 37.0601 | 31.6313 | 2.4539
| 29 | 1.233 | 10.88 | 1000 | 20 | 3 Ph | 1.233_DC | 29.592 | 43.7155 |  |  | 910.7386 | 36.9624 | 7.5335 | 14.9616 | 31.954 | 10.3572 | 10.0181 | 21.5968 | 19.2348 | 0 | 0 | 2.362 | 29.9179 | 27.5559 | -0.22963
| 30 | 1.269 | 10.88 | 600 | 20 | 3 Ph | 1.269 | 32.4 | 52.0257 |  |  | 1083.8686 | 43.9889 | 8.9657 | 17.542 | 38.0284 | 12.3261 | 11.9226 | 25.7023 | 20.0739 | 0 | 0 | 5.6284 | 38.4226 | 32.7942 | 2.5441
| 31 | 1.278 | 10.88 | 600 | 20 | 3 Ph | 1.278 | 32.6298 | 52.3947 |  |  | 1091.5556 | 44.3009 | 9.0292 | 17.6664 | 38.2981 | 12.4135 | 12.0071 | 25.8846 | 20.2163 | 0 | 0 | 5.6683 | 38.6951 | 33.0268 | 2.5622
| 32 | 1.3 | 7.92 | 1000 | 20 | 3 Ph | 1.3 | 33.1915 | 53.2966 |  |  | 1110.3461 | 45.0635 | 9.1847 | 17.9705 | 38.9574 | 12.6272 | 12.2138 | 26.3302 | 20.5643 | 0 | 0 | 5.7659 | 39.3612 | 33.5953 | 2.6063
| 33 | 1.3 | 7.92 | 1000 | 20 | 3 Ph | 1.3 | 33.1915 | 53.2966 |  |  | 1110.3461 | 45.0635 | 9.1847 | 17.9705 | 38.9574 | 12.6272 | 12.2138 | 26.3302 | 20.5643 | 0 | 0 | 5.7659 | 39.3612 | 33.5953 | 2.6063
| 34 | 1.3 | 7.92 | 1000 | 20 | 3 Ph | 1.3 | 33.1915 | 53.2966 |  |  | 1110.3461 | 45.0635 | 9.1847 | 17.9705 | 38.9574 | 12.6272 | 12.2138 | 26.3302 | 20.5643 | 0 | 0 | 5.7659 | 39.3612 | 33.5953 | 2.6063
| 35 | 1.3 | 7.92 | 1000 | 20 | 3 Ph | 1.3 | 33.1915 | 53.2966 |  |  | 1110.3461 | 45.0635 | 9.1847 | 17.9705 | 38.9574 | 12.6272 | 12.2138 | 26.3302 | 20.5643 | 0 | 0 | 5.7659 | 39.3612 | 33.5953 | 2.6063
| 36 | 1.4 | 10.56 | 1000 | 20 | 3 Ph | 1.4 | 35.7447 | 57.3964 |  |  | 1195.7573 | 48.5299 | 9.8912 | 19.3528 | 41.9541 | 13.5985 | 13.1533 | 28.3556 | 22.1462 | 0 | 0 | 6.2094 | 42.389 | 36.1796 | 2.8067
| 37 | 1.404 | 13.6 | 1000 | 20 | 3 Ph | 1.404 | 35.8468 | 57.5603 |  |  | 1199.1737 | 48.6685 | 9.9195 | 19.4081 | 42.074 | 13.6374 | 13.1909 | 28.4366 | 22.2094 | 0 | 0 | 6.2272 | 42.5101 | 36.283 | 2.8148
| 38 | 1.45 | 10.56 | 1000 | 20 | 3 Ph | 1.45 | 37.0213 | 59.4462 |  |  | 1238.4629 | 50.2631 | 10.2444 | 20.044 | 43.4525 | 14.0842 | 13.6231 | 29.3683 | 22.9371 | 0 | 0 | 6.4312 | 43.9029 | 37.4717 | 2.907
| 39 | 1.5 | 10.56 | 1000 | 20 | 3 Ph | 1.5 | 38.2979 | 61.4961 |  |  | 1281.1685 | 51.9963 | 10.5977 | 20.7352 | 44.9508 | 14.5698 | 14.0929 | 30.381 | 23.728 | 0 | 0 | 6.6529 | 45.4168 | 38.7639 | 3.0072
| 40 | 1.503 | 10.88 | 1000 | 20 | 3 Ph | 1.503 | 38.3745 | 61.6191 |  |  | 1283.7309 | 52.1003 | 10.6189 | 20.7766 | 45.0407 | 14.599 | 14.121 | 30.4417 | 23.7755 | 0 | 0 | 6.6662 | 45.5076 | 38.8414 | 3.0132
| 41 | 1.512 | 10.88 | 1000 | 20 | 3 Ph | 1.512 | 38.6043 | 61.9881 |  |  | 1291.4179 | 52.4123 | 10.6825 | 20.9011 | 45.3104 | 14.6864 | 14.2056 | 30.624 | 23.9179 | 0 | 0 | 6.7062 | 45.7801 | 39.074 | 3.0313
| 42 | 1.521 | 10.88 | 1000 | 20 | 3 Ph | 1.521 | 38.834 | 62.357 |  |  | 1299.1049 | 52.7243 | 10.7461 | 21.0255 | 45.5801 | 14.7738 | 14.2902 | 30.8063 | 24.0602 | 0 | 0 | 6.7461 | 46.0526 | 39.3065 | 3.0493
| 43 | 1.539 | 10.88 | 1000 | 20 | 3 Ph | 1.539 | 39.2936 | 63.095 |  |  | 1314.4789 | 53.3482 | 10.8732 | 21.2743 | 46.1195 | 14.9487 | 14.4593 | 31.1709 | 24.345 | 0 | 0 | 6.8259 | 46.5976 | 39.7717 | 3.0854
| 44 | 1.54 | 10.56 | 1000 | 20 | 3 Ph | 1.54 | 39.3191 | 63.136 |  |  | 1315.333 | 53.3829 | 10.8803 | 21.2881 | 46.1495 | 14.9584 | 14.4687 | 31.1911 | 24.3608 | 0 | 0 | 6.8304 | 46.6279 | 39.7976 | 3.0874
| 45 | 1.575 | 10.88 | 1000 | 20 | 3 Ph | 1.575 | 40.2128 | 64.5709 |  |  | 1345.227 | 54.5961 | 11.1276 | 21.7719 | 47.1984 | 15.2983 | 14.7975 | 31.9 | 24.9144 | 0 | 0 | 6.9856 | 47.6876 | 40.702 | 3.1576
| 46 | 1.6 | 10.56 | 1000 | 20 | 3 Ph | 1.6_DC | 38.4 | 56.7273 |  |  | 1181.8182 | 47.9642 | 9.7759 | 19.4149 | 41.465 | 13.44 | 13 | 28.025 | 24.96 | 0 | 0 | 3.065 | 38.8229 | 35.7578 | -0.29798
| 47 | 1.6 | 10.56 | 1000 | 20 | 1 Ph | 1.6 | 40.8511 | 65.5958 |  |  | 1366.5798 | 55.4627 | 11.3042 | 22.1175 | 47.9475 | 15.5412 | 15.0324 | 32.4064 | 25.3099 | 0 | 0 | 7.0965 | 48.4446 | 41.3481 | 3.2077
| 48 | 1.602 | 10.88 | 1000 | 20 | 3 Ph | 1.602 | 40.9021 | 65.6778 |  |  | 1368.288 | 55.5321 | 11.3183 | 22.1452 | 48.0075 | 15.5606 | 15.0512 | 32.4469 | 25.3415 | 0 | 0 | 7.1053 | 48.5051 | 41.3998 | 3.2117
| 49 | 1.62 | 13.6 | 1000 | 20 | 3 Ph | 1.62_DC | 38.88 | 57.4364 |  |  | 1196.5909 | 48.5637 | 9.8981 | 19.6576 | 41.9833 | 13.608 | 13.1625 | 28.3753 | 25.272 | 0 | 0 | 3.1033 | 39.3082 | 36.2048 | -0.3017
| 50 | 1.647 | 10.88 | 600 | 20 | 3 Ph | 1.647 | 42.0511 | 67.5227 |  |  | 1406.723 | 57.092 | 11.6363 | 22.7672 | 49.356 | 15.9977 | 15.474 | 33.3583 | 26.0534 | 0 | 0 | 7.3049 | 49.8676 | 42.5627 | 3.3019
| 51 | 1.683 | 13.6 | 1000 | 20 | 3 Ph | 1.683 | 42.9702 | 68.9986 |  |  | 1437.4711 | 58.3399 | 11.8906 | 23.2649 | 50.4348 | 16.3474 | 15.8122 | 34.0874 | 26.6228 | 0 | 0 | 7.4646 | 50.9576 | 43.493 | 3.3741
| 52 | 1.692 | 13.6 | 1000 | 20 | 3 Ph | 1.692 | 43.2 | 69.3676 |  |  | 1445.1581 | 58.6518 | 11.9542 | 23.3893 | 50.7045 | 16.4348 | 15.8967 | 34.2697 | 26.7652 | 0 | 0 | 7.5045 | 51.2301 | 43.7256 | 3.3921
| 53 | 1.7 | 13.2 | 1000 | 20 | 3 Ph | 1.7 | 43.4043 | 69.6956 |  |  | 1451.991 | 58.9292 | 12.0107 | 23.4999 | 50.9443 | 16.5125 | 15.9719 | 34.4318 | 26.8918 | 0 | 0 | 7.54 | 51.4724 | 43.9324 | 3.4082
| 54 | 1.7 | 10.56 | 1000 | 20 | 3 Ph | 1.7 | 43.4043 | 69.6956 |  |  | 1451.991 | 58.9292 | 12.0107 | 23.4999 | 50.9443 | 16.5125 | 15.9719 | 34.4318 | 26.8918 | 0 | 0 | 7.54 | 51.4724 | 43.9324 | 3.4082
| 55 | 1.746 | 13.6 | 1000 | 20 | 3 Ph | 1.746 | 44.5787 | 71.5814 |  |  | 1491.2802 | 60.5237 | 12.3357 | 24.1357 | 52.3227 | 16.9593 | 16.4041 | 35.3634 | 27.6194 | 0 | 0 | 7.744 | 52.8651 | 45.1211 | 3.5004
| 56 | 1.773 | 13.6 | 1000 | 20 | 1 Ph | 1.773_DC | 42.552 | 62.8609 |  |  | 1309.6023 | 53.1503 | 10.8329 | 21.5141 | 45.9484 | 14.8932 | 14.4056 | 31.0552 | 27.6588 | 0 | 0 | 3.3964 | 43.0206 | 39.6242 | -0.3302
| 57 | 1.8 | 13.2 | 1000 | 20 | 3 Ph | 1.8_DC | 43.2 | 63.8182 |  |  | 1329.5455 | 53.9597 | 10.9979 | 21.8418 | 46.6482 | 15.12 | 14.625 | 31.5282 | 28.08 | 0 | 0 | 3.4482 | 43.6757 | 40.2276 | -0.33522
| 58 | 1.8 | 13.6 | 1000 | 20 | 3 Ph | 1.8 | 45.9574 | 73.7953 |  |  | 1537.4022 | 62.3956 | 12.7172 | 24.8822 | 53.941 | 17.4838 | 16.9114 | 36.4572 | 28.4736 | 0 | 0 | 7.9835 | 54.5002 | 46.5166 | 3.6087
| 59 | 1.84 | 13.2 | 1000 | 20 | 3 Ph | 1.84 | 46.9787 | 75.4352 |  |  | 1571.5667 | 63.7821 | 12.9999 | 25.4352 | 55.1397 | 17.8723 | 17.2872 | 37.2673 | 29.1064 | 0 | 0 | 8.1609 | 55.7113 | 47.5503 | 3.6889
| 60 | 1.935 | 13.6 | 1200 | 30 | 3 Ph | 1.935_DC | 46.44 | 68.6045 |  |  | 1429.2614 | 58.0067 | 11.8227 | 23.4799 | 50.1468 | 16.254 | 15.7219 | 33.8928 | 30.186 | 0 | 0 | 3.7068 | 46.9514 | 43.2446 | -0.36037
| 61 | 1.989 | 13.6 | 1200 | 30 | 3 Ph | 1.989_DC | 47.736 | 70.5191 |  |  | 1469.1477 | 59.6255 | 12.1527 | 24.1351 | 51.5462 | 16.7076 | 16.1606 | 34.8386 | 31.0284 | 0 | 0 | 3.8102 | 48.2617 | 44.4515 | -0.37042
| 62 | 2 | 13.2 | 1200 | 20 | 3 Ph | 2 | 51.0638 | 81.9948 |  |  | 1708.2247 | 69.3284 | 14.1303 | 27.6469 | 59.9344 | 19.4265 | 18.7905 | 40.508 | 31.6374 | 0 | 0 | 8.8706 | 60.5557 | 51.6851 | 4.0096
| 63 | 2 | 13.2 | 1200 | 20 | 3 Ph | 2 | 51.0638 | 81.9948 |  |  | 1708.2247 | 69.3284 | 14.1303 | 27.6469 | 59.9344 | 19.4265 | 18.7905 | 40.508 | 31.6374 | 0 | 0 | 8.8706 | 60.5557 | 51.6851 | 4.0096
| 64 | 2.015 | 13.2 | 1200 | 20 | 3 Ph | 2.015_DC | 48.36 | 71.4409 |  |  | 1488.3523 | 60.4049 | 12.3115 | 24.4506 | 52.22 | 16.926 | 16.3719 | 35.294 | 31.434 | 0 | 0 | 3.86 | 48.8926 | 45.0325 | -0.37526
| 65 | 2.035 | 13.2 | 1200 | 20 | 3 Ph | 2.035 | 51.9574 | 83.4297 |  |  | 1738.1186 | 70.5417 | 14.3776 | 28.1307 | 60.9833 | 19.7664 | 19.1193 | 41.2168 | 32.191 | 0 | 0 | 9.0258 | 61.6155 | 52.5896 | 4.0798
| 66 | 2.043 | 13.6 | 1200 | 30 | 3 Ph | 2.043 | 52.1617 | 83.7577 |  |  | 1744.9515 | 70.819 | 14.4341 | 28.2413 | 61.223 | 19.8441 | 19.1945 | 41.3789 | 32.3176 | 0 | 0 | 9.0613 | 61.8577 | 52.7964 | 4.0958
| 67 | 2.106 | 16.32 | 1200 | 30 | 3 Ph | 2.106 | 53.7702 | 86.3405 |  |  | 1798.7606 | 73.0028 | 14.8792 | 29.1122 | 63.1109 | 20.4561 | 19.7864 | 42.6549 | 33.3142 | 0 | 0 | 9.3407 | 63.7652 | 54.4245 | 4.2221
| 68 | 2.142 | 13.6 | 1200 | 30 | 3 Ph | 2.142 | 54.6894 | 87.8164 |  |  | 1829.5087 | 74.2507 | 15.1335 | 29.6098 | 64.1898 | 20.8057 | 20.1246 | 43.384 | 33.8836 | 0 | 0 | 9.5004 | 64.8552 | 55.3548 | 4.2943
| 69 | 2.15 | 15.84 | 1200 | 20 | 3 Ph | 2.15 | 54.8936 | 88.1444 |  |  | 1836.3416 | 74.528 | 15.19 | 29.7204 | 64.4295 | 20.8834 | 20.1998 | 43.5461 | 34.0102 | 0 | 0 | 9.5359 | 65.0974 | 55.5615 | 4.3104
| 70 | 2.2 | 15.84 | 1200 | 20 | 3 Ph | 2.2 | 56.1702 | 90.1943 |  |  | 1879.0472 | 76.2613 | 15.5433 | 30.4116 | 65.9279 | 21.3691 | 20.6695 | 44.5588 | 34.8011 | 0 | 0 | 9.7576 | 66.6113 | 56.8537 | 4.4106
| 71 | 2.27 | 15.84 | 1200 | 20 | 3 Ph | 2.27_DC | 54.48 | 80.4818 |  |  | 1676.7045 | 68.0492 | 13.8695 | 27.5449 | 58.8285 | 19.068 | 18.4438 | 39.7605 | 35.412 | 0 | 0 | 4.3485 | 55.08 | 50.7314 | -0.42275
| 72 | 2.3 | 15.84 | 1200 | 20 | 3 Ph | 2.3 | 58.7234 | 94.294 |  |  | 1964.4584 | 79.7277 | 16.2498 | 31.7939 | 68.9246 | 22.3404 | 21.609 | 46.5842 | 36.383 | 0 | 0 | 10.2012 | 69.6391 | 59.4379 | 4.6111
| 73 | 2.466 | 16.32 | 2000 | 30 | 3 Ph | 2.466 | 62.9617 | 101.0996 |  |  | 2106.2411 | 85.4819 | 17.4226 | 34.0886 | 73.8991 | 23.9528 | 23.1687 | 49.9463 | 39.0089 | 0 | 0 | 10.9374 | 74.6652 | 63.7278 | 4.9439
| 74 | 2.5 | 15.84 | 1800 | 30 | 3 Ph | 2.5 | 63.8298 | 102.4935 |  |  | 2135.2809 | 86.6605 | 17.6628 | 34.5586 | 74.918 | 24.2831 | 23.4881 | 50.6349 | 39.5467 | 0 | 0 | 11.0882 | 75.6947 | 64.6064 | 5.012
| 75 | 2.5 | 15.84 | 1800 | 30 | 3 Ph | 2.5 | 63.8298 | 102.4935 |  |  | 2135.2809 | 86.6605 | 17.6628 | 34.5586 | 74.918 | 24.2831 | 23.4881 | 50.6349 | 39.5467 | 0 | 0 | 11.0882 | 75.6947 | 64.6064 | 5.012
| 76 | 2.5 | 15.84 | 1800 | 30 | 3 Ph | 2.5 | 63.8298 | 102.4935 |  |  | 2135.2809 | 86.6605 | 17.6628 | 34.5586 | 74.918 | 24.2831 | 23.4881 | 50.6349 | 39.5467 | 0 | 0 | 11.0882 | 75.6947 | 64.6064 | 5.012
| 77 | 2.511 | 16.32 | 1200 | 30 | 3 Ph | 2.511_DC | 60.264 | 89.0264 |  |  | 1854.7159 | 75.2738 | 15.342 | 30.4692 | 65.0742 | 21.0924 | 20.4019 | 43.9818 | 39.1716 | 0 | 0 | 4.8102 | 60.9276 | 56.1175 | -0.46764
| 78 | 2.56 | 15.84 | 1800 | 30 | 3 Ph | 2.56 | 65.3617 | 104.9533 |  |  | 2186.5276 | 88.7404 | 18.0867 | 35.388 | 76.7161 | 24.8659 | 24.0518 | 51.8502 | 40.4958 | 0 | 0 | 11.3544 | 77.5113 | 66.157 | 5.1323
| 79 | 2.6 | 18.48 | 1800 | 30 | 3 Ph | 2.6 | 66.383 | 106.5932 |  |  | 2220.6921 | 90.1269 | 18.3694 | 35.941 | 77.9147 | 25.2544 | 24.4276 | 52.6603 | 41.1286 | 0 | 0 | 11.5318 | 78.7224 | 67.1907 | 5.2125
| 80 | 2.601 | 16.32 | 2000 | 30 | 3 Ph | 2.601 | 66.4085 | 106.6342 |  |  | 2221.5462 | 90.1616 | 18.3764 | 35.9548 | 77.9447 | 25.2641 | 24.437 | 52.6806 | 41.1444 | 0 | 0 | 11.5362 | 78.7527 | 67.2165 | 5.2145
| 81 | 2.628 | 16.32 | 2000 | 30 | 3 Ph | 2.628 | 67.0979 | 107.7411 |  |  | 2244.6073 | 91.0975 | 18.5672 | 36.328 | 78.7538 | 25.5264 | 24.6907 | 53.2275 | 41.5715 | 0 | 0 | 11.656 | 79.5702 | 67.9143 | 5.2687
| 82 | 2.673 | 16.32 | 2000 | 30 | 3 Ph | 2.673 | 68.2468 | 109.586 |  |  | 2283.0423 | 92.6574 | 18.8851 | 36.9501 | 80.1023 | 25.9635 | 25.1135 | 54.1389 | 42.2833 | 0 | 0 | 11.8555 | 80.9327 | 69.0772 | 5.3589
| 83 | 2.7 | 16.32 | 2000 | 30 | 3 Ph | 2.7 | 68.9362 | 110.693 |  |  | 2306.1034 | 93.5934 | 19.0759 | 37.3233 | 80.9115 | 26.2257 | 25.3671 | 54.6857 | 42.7105 | 0 | 0 | 11.9753 | 81.7502 | 69.7749 | 5.413
| 84 | 2.736 | 16.32 | 2000 | 30 | 3 Ph | 2.736 | 69.8553 | 112.1689 |  |  | 2336.8514 | 94.8413 | 19.3302 | 37.821 | 81.9903 | 26.5754 | 25.7054 | 55.4149 | 43.2799 | 0 | 0 | 12.135 | 82.8402 | 70.7053 | 5.4852
| 85 | 2.772 | 19.04 | 2000 | 30 | 3 Ph | 2.772 | 70.7745 | 113.6448 |  |  | 2367.5994 | 96.0892 | 19.5846 | 38.3186 | 83.0691 | 26.9251 | 26.0436 | 56.144 | 43.8494 | 0 | 0 | 12.2946 | 83.9302 | 71.6356 | 5.5573
| 86 | 2.781 | 19.04 | 2000 | 30 | 3 Ph | 2.781 | 71.0043 | 114.0137 |  |  | 2375.2865 | 96.4012 | 19.6481 | 38.443 | 83.3388 | 27.0125 | 26.1282 | 56.3263 | 43.9918 | 0 | 0 | 12.3346 | 84.2027 | 71.8682 | 5.5754
| 87 | 2.853 | 19.04 | 2000 | 30 | 3 Ph | 2.853 | 72.8426 | 116.9656 |  |  | 2436.7825 | 98.897 | 20.1568 | 39.4383 | 85.4964 | 27.7118 | 26.8046 | 57.7846 | 45.1307 | 0 | 0 | 12.6539 | 86.3827 | 73.7289 | 5.7197
| 88 | 2.9 | 18.48 | 1800 | 30 | 3 Ph | 2.9 | 74.0426 | 118.8924 |  |  | 2476.9258 | 100.5262 | 20.4889 | 40.088 | 86.9049 | 28.1684 | 27.2462 | 58.7365 | 45.8742 | 0 | 0 | 12.8624 | 87.8058 | 74.9435 | 5.814
| 89 | 2.961 | 19.04 | 2000 | 50 | 3 Ph | 2.961_DC | 71.064 | 104.9809 |  |  | 2187.1023 | 88.7637 | 18.0915 | 35.9297 | 76.7362 | 24.8724 | 24.0581 | 51.8638 | 46.1916 | 0 | 0 | 5.6722 | 71.8466 | 66.1744 | -0.55144
| 90 | 3 | 21.12 | 1800 | 30 | 3 Ph | 3 | 76.5957 | 122.9922 |  |  | 2562.3371 | 103.9926 | 21.1954 | 41.4704 | 89.9016 | 29.1397 | 28.1857 | 60.7619 | 47.4561 | 0 | 0 | 13.3059 | 90.8336 | 77.5277 | 6.0144
| 91 | 3.114 | 19.04 | 2000 | 50 | 3 Ph | 3.114 | 79.5064 | 127.6659 |  |  | 2659.7059 | 107.9443 | 22.0008 | 43.0462 | 93.3179 | 30.247 | 29.2568 | 63.0709 | 49.2594 | 0 | 0 | 13.8115 | 94.2853 | 80.4738 | 6.243
| 92 | 3.135 | 21.12 | 1800 | 30 | 3 Ph | 3.135 | 80.0426 | 128.5268 |  |  | 2677.6422 | 108.6723 | 22.1492 | 43.3365 | 93.9472 | 30.451 | 29.4541 | 63.4962 | 49.5916 | 0 | 0 | 13.9046 | 94.9211 | 81.0165 | 6.2851
| 93 | 3.41 | 23.76 | 2000 | 50 | 3 Ph | 3.41 | 87.0638 | 139.8011 |  |  | 2912.5231 | 118.205 | 24.0921 | 47.138 | 102.1882 | 33.1221 | 32.0378 | 69.0661 | 53.9417 | 0 | 0 | 15.1244 | 103.2475 | 88.1232 | 6.8364
| 94 | 3.5 | 23.76 | 2000 | 50 | 3 Ph | 3.5 | 89.3617 | 143.4909 |  |  | 2989.3932 | 121.3247 | 24.728 | 48.3821 | 104.8852 | 33.9963 | 32.8833 | 70.8889 | 55.3654 | 0 | 0 | 15.5235 | 105.9725 | 90.449 | 7.0169
| 95 | 3.58 | 23.76 | 2000 | 50 | 3 Ph | 3.58 | 91.4043 | 146.7707 |  |  | 3057.7222 | 124.0979 | 25.2932 | 49.488 | 107.2826 | 34.7734 | 33.6349 | 72.5092 | 56.6309 | 0 | 0 | 15.8784 | 108.3948 | 92.5164 | 7.1772
| 96 | 3.6 | 23.76 | 2000 | 50 | 3 Ph | 3.6 | 91.9149 | 147.5906 |  |  | 3074.8045 | 124.7912 | 25.4345 | 49.7644 | 107.882 | 34.9676 | 33.8228 | 72.9143 | 56.9473 | 0 | 0 | 15.9671 | 109.0003 | 93.0333 | 7.2173
| 97 | 3.816 | 24.48 | 2000 | 50 | 3 Ph | 3.816 | 97.4298 | 156.4461 |  |  | 3259.2927 | 132.2786 | 26.9606 | 52.7503 | 114.3549 | 37.0657 | 35.8522 | 77.2892 | 60.3641 | 0 | 0 | 16.9251 | 115.5403 | 98.6152 | 7.6504
| 98 | 3.9 | 23.76 | 2400 | 50 | 3 Ph | 3.9 | 99.5745 | 159.8898 |  |  | 3331.0382 | 135.1904 | 27.554 | 53.9115 | 116.8721 | 37.8816 | 36.6414 | 78.9905 | 61.6929 | 0 | 0 | 17.2976 | 118.0837 | 100.786 | 7.8188
| 99 | 3.987 | 24.48 | 2000 | 50 | 3 Ph | 3.987 | 101.7957 | 163.4566 |  |  | 3405.346 | 138.2062 | 28.1687 | 55.1141 | 119.4793 | 38.7266 | 37.4588 | 80.7526 | 63.0691 | 0 | 0 | 17.6835 | 120.7178 | 103.0343 | 7.9932
| 100 | 4.1 | 26.4 | 2400 | 50 | 3 Ph | 4.1 | 104.6809 | 168.0893 |  |  | 3501.8607 | 142.1233 | 28.9671 | 56.6762 | 122.8656 | 39.8242 | 38.5205 | 83.0413 | 64.8566 | 0 | 0 | 18.1847 | 124.1392 | 105.9545 | 8.2197
| 101 | 4.1 | 26.4 | 2400 | 50 | 3 Ph | 4.1 | 104.6809 | 168.0893 |  |  | 3501.8607 | 142.1233 | 28.9671 | 56.6762 | 122.8656 | 39.8242 | 38.5205 | 83.0413 | 64.8566 | 0 | 0 | 18.1847 | 124.1392 | 105.9545 | 8.2197
| 102 | 4.2 | 26.4 | 2400 | 50 | 3 Ph | 4.2 | 107.234 | 172.1891 |  |  | 3587.2719 | 145.5897 | 29.6736 | 58.0585 | 125.8623 | 40.7956 | 39.46 | 85.0667 | 66.4385 | 0 | 0 | 18.6282 | 127.167 | 108.5388 | 8.4202
| 103 | 4.5 | 29.04 | 2400 | 50 | 3 Ph | 4.5_DC | 108 | 159.5455 |  |  | 3323.8636 | 134.8992 | 27.4947 | 54.6044 | 116.6204 | 37.8 | 36.5625 | 78.8204 | 70.2 | 0 | 0 | 8.6204 | 109.1893 | 100.5689 | -0.83806
Batch1 | 104 | 4.617 | 29.92 | 3000 | 50 | 3 Ph | 4.617 | 117.8809 | 189.285 |  |  | 3943.4367 | 160.0447 | 32.6197 | 63.8229 | 138.3586 | 44.846 | 43.3778 | 93.5126 | 73.0349 | 0 | 0 | 20.4778 | 139.7929 | 119.3151 | 9.2562
| 105 | 4.907 | 31.68 | 3000 | 50 | 3 Ph | 4.907 | 125.2851 | 201.1742 |  |  | 4191.1293 | 170.0973 | 34.6686 | 67.8317 | 147.0491 | 47.6628 | 46.1024 | 99.3863 | 77.6223 | 0 | 0 | 21.764 | 148.5735 | 126.8095 | 9.8376
Batch1 | 106 | 5.985 | 38.08 | 4000 | 50 | 3 Ph | 5.985 | 152.8085 | 245.3694 |  |  | 5111.8624 | 207.4653 | 42.2848 | 82.7334 | 179.3537 | 58.1337 | 56.2305 | 121.2201 | 94.6748 | 0 | 0 | 26.5452 | 181.213 | 154.6678 | 11.9988
Batch2 | 107 | 7.22 | 47.52 | 4000 | 50 | 3 Ph | 7.22 | 184.3404 | 296.0012 |  |  | 6166.6912 | 250.2756 | 51.0103 | 99.8053 | 216.3632 | 70.1295 | 67.8336 | 146.2337 | 114.2109 | 0 | 0 | 32.0228 | 218.6062 | 186.5834 | 14.4748
|  | 224.661 | 1575.68 | 138600 | 2880

## Batch2_DG_PV_Battery_Hybrid
|  |  | Tower Load Service Hrs | PV Table | Battery AH | Battery AH | DG factor | DG contri | Chg eff. | Batt Volts | Inv factor | PV design | DOD | rec factor | WH Eff | PV Losses | Inv Eff | MPPT Eff | PV Hrs
|  |  | 24 | 2.64 | 600 | 1000 | 0% | 0% | 94% | 48 | 1.2 | 0% | 50% | 1.2 | 88% | 9% | 92% | 95% | 4.5
Sno. | Customer Code | Tower_Total Load (Kw) AC/DC | Tower_Total Load (Kw) | DG (Recommended) | Total Energy Demand of site in KWH | Energy required from other source in KWH | DG energy required | DG rating Calculated in KVA | DG rating proposed in KVA (Recommended) | Battery Calculated AH | Battery Proposed AH (Recommended) | PV Panel capacity Calculated in KW | Actual PV Panel capacity Proposed in KW (Recommended) | Rectifier | SCC (Kw) | Inverters Capacity Calculated (Kw) | Inverters Capacity Proposed (Kw)
8 | SAO10182 | 0.8_dc | 0.8 | 3ph | 19.2 | 19.2 | 0 | 14.9903 | 20 | 909.0909 | 600 | 5.563 | 5.28 | 8.2944 | 5.563 | 1.0213
36 | SGM00880 | 1 | 1 | 3ph | 24 | 24 | 0 | 21.4594 | 20 | 1314.019 | 600 | 8.0409 | 7.92 | 8.2944 | 8.0409 | 1.2766
48 | SGT20915 | 1.021 | 1.021 | 3ph | 24.504 | 24.504 | 0 | 21.9101 | 20 | 1341.6134 | 600 | 8.2097 | 10.56 | 8.2944 | 8.2097 | 1.3034
9 | SGM00892 | 1.1_dc | 1.1 | 3ph | 26.4 | 26.4 | 0 | 20.6117 | 20 | 1250 | 600 | 7.6491 | 7.92 | 8.2944 | 7.6491 | 1.4043
13 | SGM00947 | 1.1_dc | 1.1 | 3ph | 26.4 | 26.4 | 0 | 20.6117 | 20 | 1250 | 600 | 7.6491 | 7.92 | 8.2944 | 7.6491 | 1.4043
28 | SGM00921 | 1.1 | 1.1 | 3ph | 26.4 | 26.4 | 0 | 23.6054 | 20 | 1445.4209 | 600 | 8.845 | 7.92 | 8.2944 | 8.845 | 1.4043
11 | SGM00790 | 1.11_dc | 1.11 | 3ph | 26.64 | 26.64 | 0 | 20.7991 | 20 | 1261.3636 | 600 | 7.7187 | 7.92 | 8.2944 | 7.7187 | 1.417
17 | SGM00914 | 1.2_dc | 1.2 | 3ph | 28.8 | 28.8 | 0 | 22.4855 | 20 | 1363.6364 | 600 | 8.3445 | 7.92 | 8.2944 | 8.3445 | 1.5319
42 | SGM00953 | 1.2 | 1.2 | 3ph | 28.8 | 28.8 | 0 | 25.7513 | 20 | 1576.8228 | 600 | 9.649 | 7.92 | 8.2944 | 9.649 | 1.5319
35 | SAO10144 | 1.3 | 1.3 | 3ph | 31.2 | 31.2 | 0 | 27.8973 | 20 | 1708.2247 | 1000 | 10.4531 | 7.92 | 13.824 | 10.4531 | 1.6596
37 | SGM00949 | 1.3 | 1.3 | 3ph | 31.2 | 31.2 | 0 | 27.8973 | 20 | 1708.2247 | 1000 | 10.4531 | 7.92 | 13.824 | 10.4531 | 1.6596
39 | SAO10041 | 1.3 | 1.3 | 3ph | 31.2 | 31.2 | 0 | 27.8973 | 20 | 1708.2247 | 1000 | 10.4531 | 7.92 | 13.824 | 10.4531 | 1.6596
47 | SGM00903 | 1.3 | 1.3 | 3ph | 31.2 | 31.2 | 0 | 27.8973 | 20 | 1708.2247 | 1000 | 10.4531 | 7.92 | 13.824 | 10.4531 | 1.6596
40 | SAO10045 | 1.4 | 1.4 | 3ph | 33.6 | 33.6 | 0 | 30.0432 | 20 | 1839.6266 | 1000 | 11.2572 | 10.56 | 13.824 | 11.2572 | 1.7872
24 | SGT20856 | 1.45 | 1.45 | 3ph | 34.8 | 34.8 | 0 | 31.1162 | 20 | 1905.3276 | 1000 | 11.6593 | 10.56 | 13.824 | 11.6593 | 1.8511
26 | SAO10167 | 1.5 | 1.5 | 3ph | 36 | 36 | 0 | 32.1892 | 20 | 1971.0285 | 1000 | 12.0613 | 10.56 | 13.824 | 12.0613 | 1.9149
4 | SAO10169 | 1.54 | 1.54 |  | 36.96 | 36.96 | 0 | 33.0475 | 20 | 2023.5893 | 1000 | 12.3829 | 10.56 | 13.824 |  | 1.966
19 | SGM00887 | 1.6_dc | 1.6 | 3ph | 38.4 | 38.4 | 0 | 29.9807 | 20 | 1818.1818 | 1000 | 11.126 | 10.56 | 13.824 | 11.126 | 2.0426
44 | SGT20817 | 1.6 | 1.6 | 3ph | 38.4 | 38.4 | 0 | 34.3351 | 20 | 2102.4304 | 1000 | 12.8654 | 10.56 | 13.824 | 12.8654 | 2.0426
33 | SGT31055 | 1.7 | 1.7 | 3ph | 40.8 | 40.8 | 0 | 36.481 | 20 | 2233.8323 | 1000 | 13.6695 | 13.2 | 13.824 | 13.6695 | 2.1702
45 | SGT20898 | 1.7 | 1.7 | 3ph | 40.8 | 40.8 | 0 | 36.481 | 20 | 2233.8323 | 1000 | 13.6695 | 10.56 | 13.824 | 13.6695 | 2.1702
14 | SGT30770 | 1.8_dc | 1.8 | 3ph | 43.2 | 43.2 | 0 | 33.7282 | 20 | 2045.4545 | 1000 | 12.5167 | 13.2 | 13.824 | 12.5167 | 2.2979
21 | SGT31004 | 1.84 | 1.84 | 3ph | 44.16 | 44.16 | 0 | 39.4854 | 20 | 2417.795 | 1000 | 14.7952 | 13.2 | 13.824 | 14.7952 | 2.3489
6 | SGT20800 | 2 | 2 | 3ph | 48 | 48 | 0 | 42.9189 | 20 | 2628.038 | 1200 | 16.0817 | 13.2 | 16.5888 | 16.0817 | 2.5532
32 | SGT20912 | 2 | 2 | 3ph | 48 | 48 | 0 | 42.9189 | 20 | 2628.038 | 1200 | 16.0817 | 13.2 | 16.5888 | 16.0817 | 2.5532
20 | SGT20929 | 2.015_dc | 2.015 | 3ph | 48.36 | 48.36 | 0 | 37.7569 | 20 | 2289.7727 | 1200 | 14.0118 | 13.2 | 16.5888 | 14.0118 | 2.5723
3 | SGT31022 | 2.035 | 2.035 | 1ph | 48.84 | 48.84 | 0 | 43.67 | 20 | 2674.0287 | 1200 | 16.3632 | 13.2 | 16.5888 | 16.3632 | 2.5979
31 | SGT20822 | 2.15 | 2.15 | 3ph | 51.6 | 51.6 | 0 | 46.1378 | 20 | 2825.1409 | 1200 | 17.2879 | 15.84 | 16.5888 | 17.2879 | 2.7447
30 | SGT20503 | 2.2 | 2.2 | 3ph | 52.8 | 52.8 | 0 | 47.2108 | 20 | 2890.8418 | 1200 | 17.6899 | 15.84 | 16.5888 | 17.6899 | 2.8085
10 | SGT30494 | 2.27_dc | 2.27 | 3ph | 54.48 | 54.48 | 0 | 42.5351 | 20 | 2579.5455 | 1200 | 15.785 | 15.84 | 16.5888 | 15.785 | 2.8979
7 | SGT21066 | 2.3 | 2.3 | 3ph | 55.2 | 55.2 | 0 | 49.3567 | 20 | 3022.2437 | 1200 | 18.494 | 15.84 | 16.5888 | 18.494 | 2.9362
18 | SGT20422 | 2.5 | 2.5 |  | 60 | 60 | 0 | 53.6486 | 30 | 3285.0475 | 1800 | 20.1022 | 15.84 | 24.8832 |  | 3.1915
27 | SAO10190 | 2.5 | 2.5 | 3ph | 60 | 60 | 0 | 53.6486 | 30 | 3285.0475 | 1800 | 20.1022 | 15.84 | 24.8832 | 20.1022 | 3.1915
38 | SGT21055 | 2.5 | 2.5 | 3ph | 60 | 60 | 0 | 53.6486 | 30 | 3285.0475 | 1800 | 20.1022 | 15.84 | 24.8832 | 20.1022 | 3.1915
41 | SAO10082 | 2.56 | 2.56 | 3ph | 61.44 | 61.44 | 0 | 54.9362 | 30 | 3363.8887 | 1800 | 20.5846 | 15.84 | 24.8832 | 20.5846 | 3.2681
25 | SAO10145 | 2.6 | 2.6 | 3ph | 62.4 | 62.4 | 0 | 55.7945 | 30 | 3416.4494 | 1800 | 20.9063 | 18.48 | 24.8832 | 20.9063 | 3.3191
43 | SGT10870 | 2.9 | 2.9 | 3ph | 69.6 | 69.6 | 0 | 62.2324 | 30 | 3810.6551 | 1800 | 23.3185 | 18.48 | 24.8832 | 23.3185 | 3.7021
29 | SGT20424 | 3 | 3 | 3ph | 72 | 72 | 0 | 64.3783 | 30 | 3942.057 | 1800 | 24.1226 | 21.12 | 24.8832 | 24.1226 | 3.8298
2 | SGT20775 | 3.135 | 3.135 |  | 75.24 | 75.24 | 0 | 67.2753 | 30 | 4119.4496 | 1800 | 25.2081 | 21.12 | 24.8832 |  | 4.0021
49 | SAO10199 | 3.41 | 3.41 | 3ph | 81.84 | 81.84 | 0 | 73.1767 | 50 | 4480.8048 | 2000 | 27.4194 | 23.76 | 27.648 | 27.4194 | 4.3532
16 | SAO10191 | 3.5 | 3.5 | 3ph | 84 | 84 | 0 | 75.108 | 50 | 4599.0665 | 2000 | 28.1431 | 23.76 | 27.648 | 28.1431 | 4.4681
22 | SGT30699 | 3.58 | 3.58 | 3ph | 85.92 | 85.92 | 0 | 76.8248 | 50 | 4704.188 | 2000 | 28.7863 | 23.76 | 27.648 | 28.7863 | 4.5702
23 | SGT20420 | 3.6 | 3.6 | 3ph | 86.4 | 86.4 | 0 | 77.254 | 50 | 4730.4684 | 2000 | 28.9471 | 23.76 | 27.648 | 28.9471 | 4.5957
1 | SGT21053 | 3.9 | 3.9 | 1ph | 93.6 | 93.6 | 0 | 83.6918 | 50 | 5124.6741 | 2400 | 31.3594 | 23.76 | 33.1776 | 31.3594 | 4.9787
15 | SAO10097 | 4.1 | 4.1 | 3ph | 98.4 | 98.4 | 0 | 87.9837 | 50 | 5387.4779 | 2400 | 32.9676 | 26.4 | 33.1776 | 32.9676 | 5.234
34 | SAO10185 | 4.1 | 4.1 | 3ph | 98.4 | 98.4 | 0 | 87.9837 | 50 | 5387.4779 | 2400 | 32.9676 | 26.4 | 33.1776 | 32.9676 | 5.234
46 | SGTR21029 | 4.2 | 4.2 | 3ph | 100.8 | 100.8 | 0 | 90.1296 | 50 | 5518.8798 | 2400 | 33.7717 | 26.4 | 33.1776 | 33.7717 | 5.3617
12 | SAO10098 | 4.5_dc | 4.5 | 3ph | 108 | 108 | 0 | 84.3206 | 50 | 5113.6364 | 2400 | 31.2919 | 29.04 | 33.1776 | 31.2919 | 5.7447
50 | SGT20776 | 4.907 | 4.907 | 3ph | 117.768 | 117.768 | 0 | 105.3015 | 50 | 6447.8913 | 3000 | 39.4566 | 31.68 | 41.472 | 39.4566 | 6.2643
5 | SGT20815 | 7.22 | 7.22 | 3ph | 173.28 | 173.28 | 0 | 154.9372 | 50 | 9487.2172 | 4000 | 58.0551 | 47.52 | 55.296 | 58.0551 | 9.217
| Total | 116.643 | 116.643 |  | 2799.432 | 2799.432 | 0 | 2455.4803 | 1410 | 150163.0382 | 70400 | 918.8924

## Batch1_DG_PV_Battery_Hybrid
[5 empty] | Tower Load Service Hrs | PV Table | Battery AH | Battery AH | DG factor | DG contri | Chg eff. | Batt Volts | Inv factor | PV design | DOD | rec factor | WH Eff | PV Losses | Inv Eff | MPPT Eff | PV Hrs
[5 empty] | 24 | 2.72 | 600 | 1000 | 0% | 0% | 94% | 48 | 1.2 | 0% | 50% | 1.2 | 88% | 9% | 92% | 95% | 4.5
Sno. | No. | Customer Code | YMP Site Code | Tower_Total Load (Kw)_AC/DC | Tower_Total Load (Kw) | DG (Recommended) | Total Energy Demand of site in KWH | Energy required from other source in KWH | DG energy required | DG rating Calculated in KVA | DG rating proposed in KVA (Recommended) | Battery Calculated AH | Battery Proposed AH (Recommended) | PV Panel capacity Calculated in KW | Actual PV Panel capacity Proposed in KW (Recommended) | Rectifier | SCC (Kw) | Inverters Capacity Calculated (Kw) | Inverters Capacity Proposed (Kw)
43 | 1 | SAO10087 | CSG34-DP-SAO10087 | 0.85 | 0.85 | 3ph | 20.4 | 20.4 | 0 | 18.2405 | 20 | 1116.9162 | 600 | 6.8347 | 8.16 | 8.2944 | 6.8347 | 1.0851
2 | 2 | SAO10146 | WSG02-ML-SAO10146 | 0.87 | 0.87 | 1ph | 20.88 | 20.88 | 0 | 18.6697 | 20 | 1143.1965 | 600 | 6.9956 | 8.16 | 8.2944 | 6.9956 | 1.1106
22 | 4 | SGM00938 | CSG25-YU-SGM00938 | 0.91 | 0.91 | 3ph | 21.84 | 21.84 | 0 | 19.5281 | 20 | 1195.7573 | 600 | 7.3172 | 8.16 | 8.2944 | 7.3172 | 1.1617
42 | 5 | SGT20879 | WSG06-KL-SGT20879 | 0.93 | 0.93 | 3ph | 22.32 | 22.32 | 0 | 19.9573 | 20 | 1222.0377 | 600 | 7.478 | 8.16 | 8.2944 | 7.478 | 1.1872
29 | 6 | SGM00912 | CSG15-DY-SGM00912 | 0.97 | 0.97 | 3ph | 23.28 | 23.28 | 0 | 20.8157 | 20 | 1274.5984 | 600 | 7.7996 | 8.16 | 8.2944 | 7.7996 | 1.2383
23 | 10 | SGM00937 | CSG40-AT-SGM00937 | 1.01 | 1.01 | 3ph | 24.24 | 24.24 | 0 | 21.674 | 20 | 1327.1592 | 600 | 8.1213 | 8.16 | 8.2944 | 8.1213 | 1.2894
40 | 11 | SGM00896 | CSG14-BL-SGM00896 | 1.02 | 1.02 | 3ph | 24.48 | 24.48 | 0 | 21.8886 | 20 | 1340.2994 | 600 | 8.2017 | 8.16 | 8.2944 | 8.2017 | 1.3021
30 | 13 | SGM00928 | CSG17-KN-SGM00928 | 1.03 | 1.03 | 3ph | 24.72 | 24.72 | 0 | 22.1032 | 20 | 1353.4396 | 600 | 8.2821 | 8.16 | 8.2944 | 8.2821 | 1.3149
3 | 16 | SGM00881 | CSG28-WL-SGM00881 | 1.04_dc | 1.04 | 3ph | 24.96 | 24.96 | 0 | 19.4874 | 20 | 1181.8182 | 600 | 7.2319 | 8.16 | 8.2944 | 7.2319 | 1.3277
41 | 17 | SGM00743 | CSG__-KT-SGM00743 | 1.04 | 1.04 | 3ph | 24.96 | 24.96 | 0 | 22.3178 | 20 | 1366.5798 | 600 | 8.3625 | 8.16 | 8.2944 | 8.3625 | 1.3277
26 | 19 | SAO10033 | CSG55-SL-SAO10033 | 1.11 | 1.11 | 3ph | 26.64 | 26.64 | 0 | 23.82 | 20 | 1458.5611 | 600 | 8.9254 | 8.16 | 8.2944 | 8.9254 | 1.417
36 | 20 | SGT30873 | NSG21-KT-SGT30873 | 1.12 | 1.12 | 3ph | 26.88 | 26.88 | 0 | 24.0346 | 30 | 1471.7013 | 1000 | 9.0058 | 8.16 | 13.824 | 9.0058 | 1.4298
10 | 21 | SGM00722 | CSG50-KB-SGM00722 | 1.15_dc | 1.15 | 3ph | 27.6 | 27.6 | 0 | 21.5486 | 30 | 1306.8182 | 1000 | 7.9968 | 8.16 | 13.824 | 7.9968 | 1.4681
50 | 22 | SGM00877 | CSG13-MP-SGM00877 | 1.16 | 1.16 | 3ph | 27.84 | 27.84 | 0 | 24.893 | 30 | 1524.262 | 1000 | 9.3274 | 8.16 | 13.824 | 9.3274 | 1.4809
4 | 24 | SAO10154 | CSG37-KU-SAO10154 | 1.19_dc | 1.19 | 3ph | 28.56 | 28.56 | 0 | 22.2981 | 30 | 1352.2727 | 1000 | 8.275 | 8.16 | 13.824 | 8.275 | 1.5191
6 | 25 | SGM00891 | WSG12-KL-SGM00891 | 1.19_dc | 1.19 | 3ph | 28.56 | 28.56 | 0 | 22.2981 | 30 | 1352.2727 | 1000 | 8.275 | 8.16 | 13.824 | 8.275 | 1.5191
44 | 26 | SGM00859 | WSG__-KL-SGM00859 | 1.2 | 1.2 | 3ph | 28.8 | 28.8 | 0 | 25.7513 | 30 | 1576.8228 | 1000 | 9.649 | 8.16 | 13.824 | 9.649 | 1.5319
17 | 28 | SGM00991 | NSG07-HG-SGM00991 | 1.21_dc | 1.21 | 3ph | 29.04 | 29.04 | 0 | 22.6729 | 30 | 1375 | 1000 | 8.414 | 8.16 | 13.824 | 8.414 | 1.5447
18 | 30 | SGM00901 | CSG35-KN-SGM00901 | 1.23_dc | 1.23 | 3ph | 29.52 | 29.52 | 0 | 23.0476 | 30 | 1397.7273 | 1000 | 8.5531 | 8.16 | 13.824 | 8.5531 | 1.5702
27 | 29 | SAO10092 | CSG56-WL-SAO10092 | 1.23 | 1.23 | 3ph | 29.52 | 29.52 | 0 | 26.3951 | 30 | 1616.2434 | 1000 | 9.8903 | 8.16 | 13.824 | 9.8903 | 1.5702
38 | 32 | SGT20927 | NSG04-IT-SGM20927 | 1.27 | 1.27 | 3ph | 30.48 | 30.48 | 0 | 27.2535 | 30 | 1668.8041 | 1000 | 10.2119 | 8.16 | 13.824 | 10.2119 | 1.6213
51 | 33 | SGT31021 | NSG10-TY-SGT31021 | 1.28 | 1.28 | 3ph | 30.72 | 30.72 | 0 | 27.4681 | 30 | 1681.9443 | 1000 | 10.2923 | 8.16 | 13.824 | 10.2923 | 1.634
20 | 105 | SGT20506 | WSG14-KW-SGT20506 | 1.4 | 1.4 | 3ph | 33.6 | 33.6 | 0 | 30.0432 | 30 | 1839.6266 | 1000 | 11.2572 | 10.88 | 13.824 | 11.2572 | 1.7872
45 | 106 | SGT20512 | WSG15-KW-SGT20512 | 1.5 | 1.5 | 3ph | 36 | 36 | 0 | 32.1892 | 30 | 1971.0285 | 1000 | 12.0613 | 10.88 | 13.824 | 12.0613 | 1.9149
16 | 38 | SGT31005 | CSG33-KB-SGT31005 | 1.51 | 1.51 | 3ph | 36.24 | 36.24 | 0 | 32.4038 | 30 | 1984.1687 | 1000 | 12.1417 | 10.88 | 13.824 | 12.1417 | 1.9277
46 | 39 | SGT31032 | CSG49-KO-SGT31032 | 1.52 | 1.52 | 3ph | 36.48 | 36.48 | 0 | 32.6183 | 30 | 1997.3089 | 1000 | 12.2221 | 10.88 | 13.824 | 12.2221 | 1.9404
47 | 40 | SGT30474 | CSG41-KB-SGT30474 | 1.54 | 1.54 | 3ph | 36.96 | 36.96 | 0 | 33.0475 | 30 | 2023.5893 | 1000 | 12.3829 | 10.88 | 13.824 | 12.3829 | 1.966
37 | 41 | SGT31033 | CSG31-KO-SGT31033 | 1.57 | 1.57 | 3ph | 37.68 | 37.68 | 0 | 33.6913 | 30 | 2063.0098 | 1000 | 12.6242 | 10.88 | 13.824 | 12.6242 | 2.0043
52 | 100 | SGT30698 | CSG42-KB-SGT30698 | 1.6 | 1.6 | 3ph | 38.4 | 38.4 | 0 | 34.3351 | 30 | 2102.4304 | 1000 | 12.8654 | 10.88 | 13.824 | 12.8654 | 2.0426
11 | 45 | SGT30692 | CSG47-KB-SGT30692 | 1.62_dc | 1.62 | 3ph | 38.88 | 38.88 | 0 | 30.3554 | 30 | 1840.9091 | 1000 | 11.2651 | 13.6 | 13.824 | 11.2651 | 2.0681
31 | 47 | SGT31009 | CSG23-TZ-SGT31009 | 1.65 | 1.65 | 3ph | 39.6 | 39.6 | 0 | 35.4081 | 30 | 2168.1314 | 1000 | 13.2674 | 13.6 | 13.824 | 13.2674 | 2.1064
34 | 48 | SAO10177 | NSG13-ID-SAO10177 | 1.68 | 1.68 | 3ph | 40.32 | 40.32 | 0 | 36.0519 | 30 | 2207.5519 | 1000 | 13.5087 | 13.6 | 13.824 | 13.5087 | 2.1447
53 | 51 | SGT31010 | CSG26-TZ-SGT31010 | 1.69 | 1.69 | 3ph | 40.56 | 40.56 | 0 | 36.2665 | 30 | 2220.6921 | 1000 | 13.5891 | 13.6 | 13.824 | 13.5891 | 2.1574
32 | 54 | SAO10181 | CSG54-MK-SAO10181 | 1.75 | 1.75 | 3ph | 42 | 42 | 0 | 37.554 | 30 | 2299.5333 | 1000 | 14.0715 | 13.6 | 13.824 | 14.0715 | 2.234
1 | 55 | SGT20943 | WSG22-MK-SGT20943 | 1.78_dc | 1.78 | 1ph | 42.72 | 42.72 | 0 | 33.3535 | 20 | 2022.7273 | 1000 | 12.3777 | 13.6 | 13.824 | 12.3777 | 2.2723
48 | 103 | SGT20508 | WSG24-KW-SGT20508 | 1.8 | 1.8 | 3ph | 43.2 | 43.2 | 0 | 38.627 | 30 | 2365.2342 | 1000 | 14.4736 | 13.6 | 13.824 | 14.4736 | 2.2979
8 | 58 | SGT21073 | WSG11-PB-SGT21073 | 1.93_dc | 1.93 | 3ph | 46.32 | 46.32 | 0 | 36.1642 | 30 | 2193.1818 | 1200 | 13.4207 | 13.6 | 16.5888 | 13.4207 | 2.4638
9 | 63 | SGT20875 | CSG51-SG-SGT20875 | 1.99_dc | 1.99 | 3ph | 47.76 | 47.76 | 0 | 37.2884 | 30 | 2261.3636 | 1200 | 13.838 | 13.6 | 16.5888 | 13.838 | 2.5404
19 | 64 | SGT20746 | CSG__-PL-SGT20746 | 2.05 | 2.05 | 3ph | 49.2 | 49.2 | 0 | 43.9919 | 30 | 2693.739 | 1200 | 16.4838 | 13.6 | 16.5888 | 16.4838 | 2.617
12 | 65 | SGT31017 | NSG06-KT-SGT31017 | 2.11 | 2.11 | 3ph | 50.64 | 50.64 | 0 | 45.2794 | 30 | 2772.5801 | 1200 | 16.9662 | 16.32 | 16.5888 | 16.9662 | 2.6936
54 | 66 | SAO10156 | CSG38-DP-SAO10156 | 2.14 | 2.14 | 3ph | 51.36 | 51.36 | 0 | 45.9232 | 30 | 2812.0007 | 1200 | 17.2075 | 16.32 | 16.5888 | 17.2075 | 2.7319
55 | 70 | SAO10180 | CSG27-KO-SAO10180 | 2.47 | 2.47 | 3ph | 59.28 | 59.28 | 0 | 53.0048 | 50 | 3245.6269 | 2000 | 19.861 | 16.32 | 27.648 | 19.861 | 3.1532
7 | 71 | SGT31048 | CSG24-TZ-SGT31048 | 2.51_dc | 2.51 | 3ph | 60.24 | 60.24 | 0 | 47.0322 | 50 | 2852.2727 | 2000 | 17.4539 | 16.32 | 27.648 | 17.4539 | 3.2043
28 | 75 | SGT20841 | CSG19-KB-SGT20841 | 2.6 | 2.6 | 3ph | 62.4 | 62.4 | 0 | 55.7945 | 50 | 3416.4494 | 2000 | 20.9063 | 19.04 | 27.648 | 20.9063 | 3.3191
39 | 76 | SGT20958 | WSG28-TM-SGT20958 | 2.63 | 2.63 | 3ph | 63.12 | 63.12 | 0 | 56.4383 | 50 | 3455.87 | 2000 | 21.1475 | 19.04 | 27.648 | 21.1475 | 3.3574
49 | 78 | SGT30725 | CSG43-TZ-SGT30725 | 2.67 | 2.67 | 3ph | 64.08 | 64.08 | 0 | 57.2967 | 50 | 3508.4307 | 2000 | 21.4691 | 19.04 | 27.648 | 21.4691 | 3.4085
33 | 79 | SGT20906 | WSG07-TM-SGT20906 | 2.7 | 2.7 | 3ph | 64.8 | 64.8 | 0 | 57.9405 | 50 | 3547.8513 | 2000 | 21.7104 | 19.04 | 27.648 | 21.7104 | 3.4468
13 | 81 | SGT20908 | WSG10-KP-SGT20908 | 2.74 | 2.74 | 3ph | 65.76 | 65.76 | 0 | 58.7989 | 50 | 3600.4121 | 2000 | 22.032 | 19.04 | 27.648 | 22.032 | 3.4979
25 | 82 | SGT20514 | NSG15-KT-SGT20514 | 2.77 | 2.77 | 3ph | 66.48 | 66.48 | 0 | 59.4426 | 50 | 3639.8326 | 2000 | 22.2732 | 19.04 | 27.648 | 22.2732 | 3.5362
14 | 83 | SAO10140 | NSG12-KT-SAO10140 | 2.78 | 2.78 | 3ph | 66.72 | 66.72 | 0 | 59.6572 | 50 | 3652.9728 | 2000 | 22.3536 | 19.04 | 27.648 | 22.3536 | 3.5489
56 | 85 | SGT20500 | NSG19-KT-SGT20500 | 2.85 | 2.85 | 3ph | 68.4 | 68.4 | 0 | 61.1594 | 50 | 3744.9542 | 2000 | 22.9165 | 19.04 | 27.648 | 22.9165 | 3.6383
5 | 108 | SGT20777 | NSG25-HG-SGT20777 | 2.96_dc | 2.96 | 3ph | 71.04 | 71.04 | 0 | 55.4642 | 50 | 3363.6364 | 2000 | 20.5831 | 19.04 | 27.648 | 20.5831 | 3.7787
35 | 90 | SAO10196 | CSG12-AD-SAO10196 | 3.12 | 3.12 | 3ph | 74.88 | 74.88 | 0 | 66.9535 | 50 | 4099.7393 | 2000 | 25.0875 | 21.76 | 27.648 | 25.0875 | 3.983
21 | 94 | SAO10022 | CSG11-MN-SAO10022 | 3.82 | 3.82 | 3ph | 91.68 | 91.68 | 0 | 81.9751 | 50 | 5019.5526 | 2000 | 30.7161 | 27.2 | 27.648 | 30.7161 | 4.8766
15 | 95 | SAO10161 | CSG57-PL-SAO10161 | 3.99 | 3.99 | 3ph | 95.76 | 95.76 | 0 | 85.6232 | 50 | 5242.9358 | 2000 | 32.0831 | 27.2 | 27.648 | 32.0831 | 5.0936
57 | 96 | SGT20911 | WSG08-KL-SGT20911 | 4.62 | 4.62 | 3ph | 110.88 | 110.88 | 0 | 99.1426 | 50 | 6070.7678 | 3000 | 37.1488 | 32.64 | 41.472 | 37.1488 | 5.8979
24 | 98 | SGT20936 | NSG16-IT-SGT20936 | 5.98 | 5.98 | 3ph | 143.52 | 143.52 | 0 | 128.3275 | 50 | 7857.8337 | 4000 | 48.0844 | 40.8 | 55.296 | 48.0844 | 7.634
Total |  |  |  | 132.05 | 132.05 |  |  |  |  | 2264.8062 |  | 138510.1773 |  | 847.2914
CAT1 | Tower < 60mtrs, No community load
CAT2 | Tower > 60mtrs, No community load | [8 empty] | 0 | [5 empty] | 0
CAT3 | Tower < 60mtrs with community load | [8 empty] | 0 | [5 empty] | 0
CAT4 | Tower > 60mtrs with community load | [8 empty] | 0

## PV Syst vs Actual_E_Avail_8m
|  | PV Syst Monthly Generation Data (Expected) | [9 empty] | PV Syst | Actual
| Site ID | SGM00912 |  | SAO10033 |  | SAO10092 |  | SGT31033 |  | SAO10196 |  | Average | Average | Ratio Factor of Actual v/s PV Syst Generation
| PV (kWp) | 7.8 | 7.8 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 18.2 | 18.2 | 57.2 | 57.2 | SGM00912 | SAO10033 | SAO10092 | SGT31033 | SAO10196
Days | Month | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh
31 | Jan | 1136 | 1188.2244 | 1561 | 1666.5009 | 1553 | 1618.3665 | 1559 | 1662.6457 | 2655 | 2826.4886 | 8464 | 8962.2263
28 | Feb | 1054 | 1102.4547 | 1392 | 1486.079 | 1385 | 1443.2953 | 1445 | 1541.0668 | 2425 | 2581.6327 | 7701 | 8154.5285
31 | Mar | 1140 | 1192.4083 | 1519 | 1621.6624 | 1521 | 1585.0196 | 1565 | 1669.0446 | 2631 | 2800.9384 | 8376 | 8869.0734
30 | Apr | 1106 | 1091.3 | 1465 | 1483.7 | 1456 | 1448.7 | 1468 | 1522.8 | 2559 | 2650.5 | 8054 | 8197 | 1.046 | 1.0676 | 1.0421 | 1.0665 | 1.0646
31 | May | 1054 | 1168 | 1401 | 1576 | 1395 | 1522.3 | 1423 | 1560.4 | 2451 | 2683.1 | 7724 | 8509.8
31 | Oct | 1008 | 1054.34 | 1309 | 1397.4694 | 1388 | 1446.4216 | 1371 | 1462.1471 | 2346 | 2497.5301 | 7422 | 7857.9081
30 | Nov | 1074 | 1123.3742 | 1444 | 1541.5934 | 1468 | 1529.7888 | 1464 | 1561.3299 | 2545 | 2709.3836 | 7995 | 8465.47
31 | Dec | 1174 | 1227.9714 | 1577 | 1683.5823 | 1568 | 1633.9979 | 1616 | 1723.4352 | 2735 | 2911.6559 | 8670 | 9180.6427
243 | Year | 8746 | 9148.0731 | 11668 | 12456.5874 | 11734 | 12227.8899 | 11911 | 12702.8693 | 20347 | 21661.2294 | 64406 | 68196.6491
| Specific Prod. (kWh/kWp/year | 1121.2821 | 1172.8299 | 1121.9231 | 1197.7488 | 1128.2692 | 1175.7586 | 1145.2885 | 1221.4297 | 1117.967 | 1190.1774 | 1125.979 | 1192.2491
| Specific Yield (kWh/kWp/day) | 4.6143 | 4.8265 | 4.617 | 4.929 | 4.6431 | 4.8385 | 4.7131 | 5.0265 | 4.6007 | 4.8978 | 4.6337 | 4.9064
| Highlighted in RED | To be validated once generation data received from ground.

## PV Syst vs Actual_E_Avail_12m
| PV Syst Monthly Generation Data (Expected) | [9 empty] | PV Syst | Actual
Site ID | SGM00912 |  | SAO10033 |  | SAO10092 |  | SGT31033 |  | SAO10196 |  | Average | Average | Ratio Factor of Actual v/s PV Syst Generation
PV (kWp) | 7.8 | 7.8 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 18.2 | 18.2 | 57.2 | 57.2 | SGM00912 | SAO10033 | SAO10092 | SGT31033 | SAO10196
Month | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh | E-Avail kWh | Actual kWh
Jan | 1136 | 1188.2244 | 1561 | 1666.5009 | 1553 | 1618.3665 | 1559 | 1662.6457 | 2655 | 2826.4886 | 8464 | 8962.2263
Feb | 1054 | 1102.4547 | 1392 | 1486.079 | 1385 | 1443.2953 | 1445 | 1541.0668 | 2425 | 2581.6327 | 7701 | 8154.5285
Mar | 1140 | 1192.4083 | 1519 | 1621.6624 | 1521 | 1585.0196 | 1565 | 1669.0446 | 2631 | 2800.9384 | 8376 | 8869.0734
Apr | 1106 | 1091.3 | 1465 | 1483.7 | 1456 | 1448.7 | 1468 | 1522.8 | 2559 | 2650.5 | 8054 | 8197 | 1.046 | 1.0676 | 1.0421 | 1.0665 | 1.0646
May | 1054 | 1168 | 1401 | 1576 | 1395 | 1522.3 | 1423 | 1560.4 | 2451 | 2683.1 | 7724 | 8509.8
Jun | 932 | 974.8461 | 1242 | 1325.9412 | 1219 | 1270.3083 | 1293 | 1378.9615 | 2178 | 2318.6788 | 6864 | 7268.7359
Jul | 767 | 802.2607 | 990 | 1056.9096 | 971 | 1011.8699 | 1034 | 1102.7426 | 1751 | 1864.0985 | 5513 | 5837.8813
Aug | 758 | 792.8469 | 1014 | 1082.5317 | 1057 | 1101.4897 | 1049 | 1118.7398 | 1766 | 1880.0674 | 5644 | 5975.6755
Sep | 833 | 871.2949 | 1092 | 1165.8033 | 1217 | 1268.2241 | 1183 | 1261.6484 | 1970 | 2097.2439 | 6295 | 6664.2147
Oct | 1008 | 1054.34 | 1309 | 1397.4694 | 1388 | 1446.4216 | 1371 | 1462.1471 | 2346 | 2497.5301 | 7422 | 7857.9081
Nov | 1074 | 1123.3742 | 1444 | 1541.5934 | 1468 | 1529.7888 | 1464 | 1561.3299 | 2545 | 2709.3836 | 7995 | 8465.47
Dec | 1174 | 1227.9714 | 1577 | 1683.5823 | 1568 | 1633.9979 | 1616 | 1723.4352 | 2735 | 2911.6559 | 8670 | 9180.6427
Year | 12036 | 12589.3217 | 16006 | 17087.7733 | 16198 | 16879.7818 | 16470 | 17564.9616 | 28012 | 29821.318 | 88722 | 93943.1564
Specific Prod. (kWh/kWp/year | 1543.0769 | 1614.0156 | 1539.0385 | 1643.0551 | 1557.5 | 1623.0559 | 1583.6538 | 1688.9386 | 1539.1209 | 1638.534 | 1551.0839 | 1642.3629
Specific Yield (kWh/kWp/day) | 4.2276 | 4.422 | 4.2165 | 4.5015 | 4.2671 | 4.4467 | 4.3388 | 4.6272 | 4.2168 | 4.4891 | 4.2495 | 4.4996
Highlighted in RED | To be validated once generation data received from ground.

## Actual Generation
New Sites PV Monthly Generation Data
Site ID | SGT20875 | SAO10092 | SGT31033 | SGM00937 | SAO10022 | SAO10196 | SGM00912 | SAO10140 | SGT20514 | SGT31017 | SGM00928 | SGT20927 | SGM00722 | SAO10181 | SAO10033 | SGT31010 | SGT20911 | SGT31009
PV (kWP) | 13 | 10.4 | 10.4 | 10.4 | 23.4 | 18.2 | 7.8 | 18.2 | 18.2 | 15.6 | 10.4 | 10.4 | 10.4 | 13 | 10.4 | 13 | 28.6 | 10.4
COD | 2019-03-10 | 2019-03-13 | 2019-03-15 | 2019-03-16 | 2019-03-16 | 2019-03-19 | 2019-03-19 | 2019-03-21 | 2019-03-22 | 2019-03-22 | 2019-03-23 | 2019-03-25 | 2019-03-27 | 2019-03-27 | 2019-03-28 | 2019-03-28 | 2019-03-29 | 2019-03-29
Month | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
Mar'19 | 264.7 | 907.6 | 750.6 | 628.4 | 1149.4 | 937.7 | 476.5 | 944.4 | 896.7 | 650.6 | 336.8 | 225.3 | 194.9 | 218.2 | 94 | 198.1 | 293.8 | 109.4
Apr'19 | 1205 | 1448.7 | 1522.8 | 900.5 | 2828.8 | 2650.5 | 1091.3 | 2641.9 | 2441.3 | 1996.6 | 1246.3 | 972.5 | 1286.1 | 1724.6 | 1483.7 | 1683.7 | 3433.9 | 1079.2 | Avg for 18 sites
May'19 | 1362 | 1522.3 | 1522.8 | 1037.2 | 3058 | 2683.1 | 1168 | 2476.6 | 2480.7 | 1973.2 | 1331.9 | 1030.4 | 1366.9 | 1746.8 | 1576 | 1664.2 | 3757.6 | 1161.8
Specific Yield (kwh/kWp/day)_Apr19 | 3.0897 | 4.6433 | 4.8808 | 2.8862 | 4.0296 | 4.8544 | 4.6637 | 4.8386 | 4.4712 | 4.2662 | 3.9946 | 3.117 | 4.1221 | 4.4221 | 4.7554 | 4.3172 | 4.0022 | 3.459 | 4.1563
Specific Yield (kwh/kWp/day)_May19 | 3.3797 | 4.7218 | 4.7233 | 3.2171 | 4.2156 | 4.7556 | 4.8304 | 4.3896 | 4.3968 | 4.0802 | 4.1312 | 3.196 | 4.2398 | 4.3345 | 4.8883 | 4.1295 | 4.2382 | 3.6036 | 4.1929
Pilot Sites PV syst Monthly Generation Data (Expected )
Site ID | SG1089 | SG1081 | SGG00905 | SGT21039
PV (kWP) | 15.6 | 15.6 | 15.6 | 15.6
Month | kWh | kWh | kWh | kWh
Mar'2018 | 1551.8731 | 1494.3681 | 1169.073 | 1420.888
Apr'2018 | 1388.2311 | 1809.0461 | 1301.628 | 1540.735
May'2018 | 1340.8081 | 1486.2551 | 1340.443 | 1948.038
Jun'2018 | 1374.8461 | 1272.1171 | 1243.224 | 1563.607
Jul'2018 | 1385.0621 | 1613.6741 | 436.528 | 1592.851
Aug'2018 | 1228.5751 | 1551.8281 | 421.058 | 1552.862
Sep'2019 | 260.243 | 277.831 | 429.116 | 1773.656
Oct'2018 | 665.258 | 966.323 | 382.979 | 1354.872
Nov'2018 | 1428.6211 | 1803.4671 | 359.779 | 1629.737
Dec'2018 | 1386.8671 | 1674.5031 | 351.033 | 1576.649
Jan'2019 | 1473.6471 | 1706.9551 | 175.098 | 1755.471
Feb'2019 | 309.277 | 440.925 | 224.531 | 1501.599
Mar'2019 | 52.891 | 134.875 | 406.067 | 2032.856
Year (Mar- 2018 to Mar - 2019 ) | 13846.1997 | 16232.1678 | 8240.557 | 21243.821
Specific Yield (kwh/kWp/day) | 2.247 | 2.6342 | 1.3373 | 3.4476
| SAO10022 | 2828.8
| SAO10033 | 1483.7
| SAO10092 | 1448.7
| SAO10093 | 3782.1
| SAO10140 | 2641.9
| SAO10169 | 27.3
| SAO10177 | 359.3
| SAO10180 | 2337
| SAO10181 | 1724.6
| SAO10185 | 4.3
| SAO10196 | 2650.5
| SGM00722 | 1286.1
| SGM00743 | 209.4
| SGM00877 | 0
| SGM00887 | 1188.3
| SGM00896 | 1026.7
| SGM00912 | 1091.3
| SGM00928 | 1246.3
| SGM00937 | 900.5
| SGM00953 | 971.2
| SGT10870 | 112.3
| SGT20500 | 2610.2
| SGT20514 | 2441.3
| SGT20775 | 19.5
| SGT20841 | 0
| SGT20875 | 1205
| SGT20898 | 1
| SGT20906 | 1588
| SGT20908 | 1521.5
| SGT20911 | 3433.9
| SGT20912 | 1086.5
| SGT20927 | 972.5
| SGT20936 | 1.4
| SGT20958 | 1326.6
| SGT21066 | 1234.6
| SGT30725 | 2185.7
| SGT30873 | 1075
| SGT31004 | 0
| SGT31005 | 1296.9
| SGT31009 | 1079.2
| SGT31010 | 1683.7
| SGT31017 | 1996.6
| SGT31021 | 985.9
| SGT31033 | 1522.8
| SGT21041 | 2093
| SGT20800 | 1691.31
| SGT21039 | 587.571

## Batch2
Sl.No | Site Code | CW batch | Tower Load AC/DC | Total BTS Load (KW) | DC /AC Solution | PV (kWp) (330Wp*8nos=2.64kWp*n) | Battery Bank 48V (Ah) | Genset (kVA) | Genset Type (1 Ph/ 3Ph)
8 | SAO10182 | Batch 2 | 0.8_dc | 0.8 | DC | 5.28 | 600 | 20 | 3 Ph
36 | SGM00880 | Batch 2 | 1 | 1 | AC | 7.92 | 600 | 20 | 3 Ph
48 | SGT20915 | Batch 2 | 1.021 | 1.021 | AC | 10.56 | 600 | 20 | 3 Ph
9 | SGM00892 | Batch 2 | 1.1_dc | 1.1 | DC | 7.92 | 600 | 20 | 3 Ph
13 | SGM00947 | Batch 2 | 1.1_dc | 1.1 | DC | 7.92 | 600 | 20 | 3 Ph
28 | SGM00921 | Batch 2 | 1.1 | 1.1 | AC | 7.92 | 600 | 20 | 1 Ph
11 | SGM00790 | Batch 2 | 1.11_dc | 1.11 | DC | 7.92 | 600 | 20 | 3 Ph
17 | SGM00914 | Batch 2 | 1.2_dc | 1.2 | DC | 7.92 | 600 | 20 | 3 Ph
42 | SGM00953 | Batch 2 | 1.2 | 1.2 | AC | 7.92 | 600 | 20 | 3 Ph
35 | SAO10144 | Batch 2 | 1.3 | 1.3 | AC | 7.92 | 1000 | 20 | 3 Ph
37 | SGM00949 | Batch 2 | 1.3 | 1.3 | AC | 7.92 | 1000 | 20 | 3 Ph
39 | SAO10041 | Batch 2 | 1.3 | 1.3 | AC | 7.92 | 1000 | 20 | 3 Ph
47 | SGM00903 | Batch 2 | 1.3 | 1.3 | AC | 7.92 | 1000 | 20 | 3 Ph
40 | SAO10045 | Batch 2 | 1.4 | 1.4 | AC | 10.56 | 1000 | 20 | 3 Ph
24 | SGT20856 | Batch 2 | 1.45 | 1.45 | AC | 10.56 | 1000 | 20 | 3 Ph
26 | SAO10167 | Batch 2 | 1.5 | 1.5 | AC | 10.56 | 1000 | 20 | 3 Ph
4 | SAO10169 | Batch 2 | 1.54 | 1.54 | AC | 10.56 | 1000 | 20 | 3 Ph
19 | SGM00887 | Batch 2 | 1.6_dc | 1.6 | DC | 10.56 | 1000 | 20 | 3 Ph
44 | SGT20817 | Batch 2 | 1.6 | 1.6 | AC | 10.56 | 1000 | 20 | 1 Ph
33 | SGT31055 | Batch 2 | 1.7 | 1.7 | AC | 13.2 | 1000 | 20 | 3 Ph
45 | SGT20898 | Batch 2 | 1.7 | 1.7 | AC | 10.56 | 1000 | 20 | 3 Ph
14 | SGT30770 | Batch 2 | 1.8_dc | 1.8 | DC | 13.2 | 1000 | 20 | 3 Ph
21 | SGT31004 | Batch 2 | 1.84 | 1.84 | AC | 13.2 | 1000 | 20 | 3 Ph
6 | SGT20800 | Batch 2 | 2 | 2 | AC | 13.2 | 1200 | 20 | 3 Ph
32 | SGT20912 | Batch 2 | 2 | 2 | AC | 13.2 | 1200 | 20 | 3 Ph
20 | SGT20929 | Batch 2 | 2.015_dc | 2.015 | DC | 13.2 | 1200 | 20 | 3 Ph
3 | SGT31022 | Batch 2 | 2.035 | 2.035 | AC | 13.2 | 1200 | 20 | 3 Ph
31 | SGT20822 | Batch 2 | 2.15 | 2.15 | AC | 15.84 | 1200 | 20 | 3 Ph
30 | SGT20503 | Batch 2 | 2.2 | 2.2 | AC | 15.84 | 1200 | 20 | 3 Ph
10 | SGT30494 | Batch 2 | 2.27_dc | 2.27 | DC | 15.84 | 1200 | 20 | 3 Ph
7 | SGT21066 | Batch 2 | 2.3 | 2.3 | AC | 15.84 | 1200 | 20 | 3 Ph
18 | SGT20422 | Batch 2 | 2.5 | 2.5 | AC | 15.84 | 1800 | 30 | 3 Ph
27 | SAO10190 | Batch 2 | 2.5 | 2.5 | AC | 15.84 | 1800 | 30 | 3 Ph
38 | SGT21055 | Batch 2 | 2.5 | 2.5 | AC | 15.84 | 1800 | 30 | 3 Ph
41 | SAO10082 | Batch 2 | 2.56 | 2.56 | AC | 15.84 | 1800 | 30 | 3 Ph
25 | SAO10145 | Batch 2 | 2.6 | 2.6 | AC | 18.48 | 1800 | 30 | 3 Ph
43 | SGT10870 | Batch 2 | 2.9 | 2.9 | AC | 18.48 | 1800 | 30 | 3 Ph
29 | SGT20424 | Batch 2 | 3 | 3 | AC | 21.12 | 1800 | 30 | 3 Ph
2 | SGT20775 | Batch 2 | 3.135 | 3.135 | AC | 21.12 | 1800 | 30 | 3 Ph
49 | SAO10199 | Batch 2 | 3.41 | 3.41 | AC | 23.76 | 2000 | 50 | 3 Ph
16 | SAO10191 | Batch 2 | 3.5 | 3.5 | AC | 23.76 | 2000 | 50 | 3 Ph
22 | SGT30699 | Batch 2 | 3.58 | 3.58 | AC | 23.76 | 2000 | 50 | 3 Ph
23 | SGT20420 | Batch 2 | 3.6 | 3.6 | AC | 23.76 | 2000 | 50 | 3 Ph
1 | SGT21053 | Batch 2 | 3.9 | 3.9 | AC | 23.76 | 2400 | 50 | 3 Ph
15 | SAO10097 | Batch 2 | 4.1 | 4.1 | AC | 26.4 | 2400 | 50 | 3 Ph
34 | SAO10185 | Batch 2 | 4.1 | 4.1 | AC | 26.4 | 2400 | 50 | 3 Ph
46 | SGTR21029 | Batch 2 | 4.2 | 4.2 | AC | 26.4 | 2400 | 50 | 3 Ph
12 | SAO10098 | Batch 2 | 4.5_dc | 4.5 | DC | 29.04 | 2400 | 50 | 3 Ph
50 | SGT20776 | Batch 2 | 4.907 | 4.907 | AC | 31.68 | 3000 | 50 | 3 Ph
5 | SGT20815 | Batch 2 | 7.22 | 7.22 | AC | 47.52 | 4000 | 50 | 3 Ph
For Array of 8 Modules (2.72kWp) |  |  | 116.643 | 116.643 |  | 781.44 | 70400 | 1410

## Batch1
| sno. | Customer Code | YMP Site Code | Tower Load AC/DC | Tower Load | PV (kWp) (340Wp*8nos=2.72kWp*n) | Battery Bank 48V (Ah) | Genset (kVA) | Genset Type (1 Ph/ 3Ph) (Recommended)
| 43 | SAO10087 | CSG34-DP-SAO10087 | 0.846 | 0.846 | 8.16 | 600 | 20 | 3 Ph | 1.97
| 2 | SAO10146 | WSG02-ML-SAO10146 | 0.864 | 0.864 | 8.16 | 600 | 20 | 1 Ph | 0.96
| 22 | SGM00938 | CSG25-YU-SGM00938 | 0.909 | 0.909 | 8.16 | 600 | 20 | 3 Ph | 1.15
| 42 | SGT20879 | WSG06-KL-SGT20879 | 0.927 | 0.927 | 8.16 | 600 | 20 | 3 Ph | 1.32
| 29 | SGM00912 | CSG15-DY-SGM00912 | 0.972 | 0.972 | 8.16 | 600 | 20 | 3 Ph | 3.29
| 23 | SGM00937 | CSG40-AT-SGM00937 | 1.008 | 1.008 | 10.88 | 600 | 20 | 3 Ph | 1.32
| 40 | SGM00896 | CSG14-BL-SGM00896 | 1.017 | 1.017 | 10.88 | 600 | 20 | 3 Ph | 2.79
| 30 | SGM00928 | CSG17-KN-SGM00928 | 1.026 | 1.026 | 10.88 | 600 | 20 | 3 Ph | 2.15
DC Distribution | 3 | SGM00881 | CSG28-WL-SGM00881 | 1.035_dc | 1.035 | 10.88 | 600 | 20 | 3 Ph | 2.21
| 41 | SGM00743 | CSG__-KT-SGM00743 | 1.044 | 1.044 | 10.88 | 600 | 20 | 3 Ph | 1.28
| 26 | SAO10033 | CSG55-SL-SAO10033 | 1.107 | 1.107 | 10.88 | 600 | 20 | 3 Ph | 1.8
| 36 | SGT30873 | NSG21-KT-SGT30873 | 1.125 | 1.125 | 10.88 | 600 | 20 | 3 Ph | 2.34
DC Distribution | 10 | SGM00722 | CSG50-KB-SGM00722 | 1.152_dc | 1.152 | 10.88 | 600 | 20 | 3 Ph | 3.04
| 50 | SGM00877 | CSG13-MP-SGM00877 | 1.161 | 1.161 | 10.88 | 600 | 20 | 3 Ph | 3.09
DC Distribution | 4 | SAO10154 | CSG37-KU-SAO10154 | 1.188_dc | 1.188 | 10.88 | 600 | 20 | 3 Ph | 4.43
DC Distribution | 6 | SGM00891 | WSG12-KL-SGM00891 | 1.188_dc | 1.188 | 10.88 | 600 | 20 | 3 Ph | 1.68
| 44 | SGM00859 | WSG__-KL-SGM00859 | 1.197 | 1.197 | 10.88 | 600 | 20 | 3 Ph | 1.35
DC Distribution | 17 | SGM00991 | NSG07-HG-SGM00991 | 1.215_dc | 1.215 | 10.88 | 1000 | 20 | 3 Ph | 1.37
| 27 | SAO10092 | CSG56-WL-SAO10092 | 1.224 | 1.224 | 10.88 | 1000 | 20 | 3 Ph | 2.27
DC Distribution | 18 | SGM00901 | CSG35-KN-SGM00901 | 1.233_dc | 1.233 | 10.88 | 1000 | 20 | 3 Ph | 1.56
| 38 | SGT20927 | NSG04-IT-SGM20927 | 1.269 | 1.269 | 10.88 | 600 | 20 | 3 Ph | 4.24
| 51 | SGT31021 | NSG10-TY-SGT31021 | 1.278 | 1.278 | 10.88 | 600 | 20 | 3 Ph | 1.01
| 20 | SGT20506 | WSG14-KW-SGT20506 | 1.404 | 1.404 | 13.6 | 1000 | 20 | 3 Ph | 1.12
| 45 | SGT20512 | WSG15-KW-SGT20512 | 1.503 | 1.503 | 10.88 | 1000 | 20 | 3 Ph | 6.65
| 16 | SGT31005 | CSG33-KB-SGT31005 | 1.512 | 1.512 | 10.88 | 1000 | 20 | 3 Ph | 3.08
| 46 | SGT31032 | CSG49-KO-SGT31032 | 1.521 | 1.521 | 10.88 | 1000 | 20 | 3 Ph | 1.23
| 47 | SGT30474 | CSG41-KB-SGT30474 | 1.539 | 1.539 | 10.88 | 1000 | 20 | 3 Ph | 1.36
| 37 | SGT31033 | CSG31-KO-SGT31033 | 1.575 | 1.575 | 10.88 | 1000 | 20 | 3 Ph | 2.89
| 52 | SGT30698 | CSG42-KB-SGT30698 | 1.602 | 1.602 | 10.88 | 1000 | 20 | 3 Ph | 1.08
DC Distribution | 11 | SGT30692 | CSG47-KB-SGT30692 | 1.62_dc | 1.62 | 13.6 | 1000 | 20 | 3 Ph | 1.14
| 31 | SGT31009 | CSG23-TZ-SGT31009 | 1.647 | 1.647 | 10.88 | 600 | 20 | 3 Ph | 1.83
| 34 | SAO10177 | NSG13-ID-SAO10177 | 1.683 | 1.683 | 13.6 | 1000 | 20 | 3 Ph | 1.94
| 53 | SGT31010 | CSG26-TZ-SGT31010 | 1.692 | 1.692 | 13.6 | 1000 | 20 | 3 Ph | 3
| 32 | SAO10181 | CSG54-MK-SAO10181 | 1.746 | 1.746 | 13.6 | 1000 | 20 | 3 Ph | 1.87
DC Distribution | 1 | SGT20943 | WSG22-MK-SGT20943 | 1.773_dc | 1.773 | 13.6 | 1000 | 20 | 1 Ph | 3.46
| 48 | SGT20508 | WSG24-KW-SGT20508 | 1.8 | 1.8 | 13.6 | 1000 | 20 | 3 Ph | 1.25
DC Distribution | 8 | SGT21073 | WSG11-PB-SGT21073 | 1.935_dc | 1.935 | 13.6 | 1200 | 30 | 3 Ph | 1.75
DC Distribution | 9 | SGT20875 | CSG51-SG-SGT20875 | 1.989_dc | 1.989 | 13.6 | 1200 | 30 | 3 Ph | 1.41
| 19 | SGT20746 | CSG__-PL-SGT20746 | 2.043 | 2.043 | 13.6 | 1200 | 30 | 3 Ph | 2.92
| 12 | SGT31017 | NSG06-KT-SGT31017 | 2.106 | 2.106 | 16.32 | 1200 | 30 | 3 Ph | 1.13
| 54 | SAO10156 | CSG38-DP-SAO10156 | 2.142 | 2.142 | 13.6 | 1200 | 30 | 3 Ph | 1.16
| 55 | SAO10180 | CSG27-KO-SAO10180 | 2.466 | 2.466 | 16.32 | 2000 | 30 | 3 Ph | 1.03
DC Distribution | 7 | SGT31048 | CSG24-TZ-SGT31048 | 2.511_dc | 2.511 | 16.32 | 1200 | 30 | 3 Ph | 0.94
| 28 | SGT20841 | CSG19-KB-SGT20841 | 2.601 | 2.601 | 16.32 | 2000 | 30 | 3 Ph | 1.33
| 39 | SGT20958 | WSG28-TM-SGT20958 | 2.628 | 2.628 | 16.32 | 2000 | 30 | 3 Ph | 1.67
| 49 | SGT30725 | CSG43-TZ-SGT30725 | 2.673 | 2.673 | 16.32 | 2000 | 30 | 3 Ph | 1.69
| 33 | SGT20906 | WSG07-TM-SGT20906 | 2.7 | 2.7 | 16.32 | 2000 | 30 | 3 Ph | 1.71
| 13 | SGT20908 | WSG10-KP-SGT20908 | 2.736 | 2.736 | 16.32 | 2000 | 30 | 3 Ph | 2
| 25 | SGT20514 | NSG15-KT-SGT20514 | 2.772 | 2.772 | 19.04 | 2000 | 30 | 3 Ph | 2.97
| 14 | SAO10140 | NSG12-KT-SAO10140 | 2.781 | 2.781 | 19.04 | 2000 | 30 | 3 Ph | 1.29
| 56 | SGT20500 | NSG19-KT-SGT20500 | 2.853 | 2.853 | 19.04 | 2000 | 30 | 3 Ph | 1.42
DC Distribution | 5 | SGT20777 | NSG25-HG-SGT20777 | 2.961_dc | 2.961 | 19.04 | 2000 | 50 | 3 Ph | 1.78
| 35 | SAO10196 | CSG12-AD-SAO10196 | 3.114 | 3.114 | 19.04 | 2000 | 50 | 3 Ph | 1.88
| 21 | SAO10022 | CSG11-MN-SAO10022 | 3.816 | 3.816 | 24.48 | 2000 | 50 | 3 Ph | 2.38
| 15 | SAO10161 | CSG57-PL-SAO10161 | 3.987 | 3.987 | 24.48 | 2000 | 50 | 3 Ph | 2.74
| 57 | SGT20911 | WSG08-KL-SGT20911 | 4.617 | 4.617 | 29.92 | 3000 | 50 | 3 Ph | 3.17
| 24 | SGT20936 | NSG16-IT-SGT20936 | 5.985 | 5.985 | 38.08 | 4000 | 50 | 3 Ph | 5.13
| For Array of 8 Modules (2.72kWp) |  |  | 108.018 | 108.018 | 794.24 | 68200 | 1470

## Percentage_File
Percentage_File
0%
1%
2%
3%
4%
5%
6%
7%
8%
9%
10%
11%
12%
13%
14%
15%
16%
17%
18%
19%
20%
21%
22%
23%
24%
25%
26%
27%
28%
29%
30%
31%
32%
33%
34%
35%
36%
37%
38%
39%
40%
41%
42%
43%
44%
45%
46%
47%
48%
49%
50%
51%
52%
53%
54%
55%
56%
57%
58%
59%
60%
61%
62%
63%
64%
65%
66%
67%
68%
69%
70%
71%
72%
73%
74%
75%
76%
77%
78%
79%
80%
81%
82%
83%
84%
85%
86%
87%
88%
89%
90%
91%
92%
93%
94%
95%
96%
97%
98%
99%
100%